## AB2_DX2712-Tirathai (hidden)
DISTRIBUTION TRANSFORMER
FORM PD 111,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB2
BIDDER |  | IN CONSORTIUM |  |  |  | ITEM NO. |  |  | 1AB2-1
a. | Manufacturer / Country |  |  |  |  | Tirathai Public Co.,Ltd./Thailand
b. | Type |  |  |  |  | 3 Ph, Outdoor oil immersed distribution Tr.
c. | Applied Standards |  |  |  |  | IEEE C57.12, TIS 384
d. | Max. Continuous Rated Capacity |  |  |  |  | 500 | [7 empty] | kVA
e. | Rated Voltage |  | - HV / LV |  |  | 22 |  |  |  | 0.4 |  |  |  | kV
f. | Rated Current |  | - HV / LV |  |  | 13.1 |  |  |  | 721-7 |  |  |  | A
g. | Impedance Voltage at Rated Voltage,
| Current, Frequency and 75 °C |  |  |  |  | ≥ 6.0 | [7 empty] | %
h. | Basic Insulation Level (BIL) of Windings
|  |  | - HV Winding |  |  | 150 | [7 empty] | kV
|  |  | - LV Winding |  |  | 30 | [7 empty] | kV
|  |  | - Neutral |  |  | 30 | [7 empty] | kV
i. | Vector Group |  |  |  |  | Dyn1
j. | Polarity |  |  |  |  | Subtractive
k. | Off Load Tap Changer
|  |  | - Manufacturer / Country |  |  | Tirathai PLC. / Thailand
|  |  | - Type / Model No. |  |  | BIL 200kV, 63A
|  |  | - Tapping Range |  |  | ± 2.5, ± 5 |  |  | % on |  | HV |  |  | Side
l. | Exciting Current in % of Full Load Current
| at 110 % / 100% / 90% / 80% Rated Voltage |  |  |  |  | 8.98 |  | 0.86 |  | 0.31 |  |  | 0.21 | %
m. | Efficiency with 0.9 Lagging Pf. Load
| at 110 % / 100% / 50% Load |  |  |  |  | 98.57 |  |  | 98.66 |  |  | 99.03 |  | %
n. | Max. Short Circuit Current which the Transformer
shall be able to withstand
|  | Symmetrical |  | - HV / LV Winding |  | 0.13 |  |  |  | 12.03 |  |  |  | kA rms
|  | Asymmetrical |  | - HV / LV Winding |  | 0.28 |  |  |  | 27.05 |  |  |  | kA peak
o. | Temperature Rise
|  | - Average Winding / Hottest Spot |  |  |  | 55 |  |  |  | 65 |  |  |  | °C
|  | - Insulating Oil |  |  |  | 55 | [7 empty] | °C
p. | Insulating Material
|  | Winding Insulation Paper |  |  | - Manufacturer | Miki / Japan
[5 empty] | - Temp. Class | A (105 C)
|  | Other Insulating Material |  |  | - Manufacturer | Weidmann / Switzerland
[5 empty] | - Temp. Class | A (105 C)
q. | Internal Gas Pressure Withstanding of Tank |  |  |  |  | 0.7 | [7 empty] | kg/cm2
r. | Insulating Oil |  | - Type |  |  |  | Uninhibited |  |  | X |  | Inhibited
|  |  | - Manufacturer |  |  | PSP / Thailand
|  |  | - Manufacturer Type |  |  | Transform Inh
|  |  | - Applied Standard |  |  | IEC 60296
Remark
s. | Bushing |  |  |  |  | HV |  |  | LV |  |  | Neutral
|  |  | - Manufacturer |  |  | Tirathai/Thailand |  |  | Tirathai/Thailand |  |  | Tirathai/Thailand
|  |  | - Type (Condenser or Solid) |  |  | Solid |  |  | Solid |  |  | Solid
|  |  | - Model No. |  |  | 30 NF 100 |  |  | 1 NF 1000 |  |  | 1 NF 1000
|  |  | - BIL |  |  | 200 |  |  | 30 |  |  | 30 |  | kV
|  |  | - Power Freq. Withstand (Dry) |  |  | 80 |  |  | 10 |  |  | 10 |  | kV
|  |  | - Power Freq. Withstand (Wet) |  |  | 75 |  |  | 10 |  |  | 10 |  | kV
|  |  | - Rated Current |  |  | 100 |  |  | 1000 |  |  | 1000 |  | A
|  |  | - Creepage Distance |  |  | 667 |  |  | 75 |  |  | 75 |  | mm
t. | Cable Terminations
|  |  | - Manufacturer |  |  | 3M
|  |  | - Type / Model / Cat. No. |  |  | Outdoor (Cold Shrink) / QT-II 5652
|  |  | - Material of External Insulator |  |  | Silicone Rubber
|  |  | - Rated Voltage |  |  | Insulation Class 25kV | [7 empty] | kV
|  |  | - Current Rating |  |  | As per Standard | [7 empty] | A
|  |  | - BIL |  |  | 150 | [7 empty] | kV
|  |  | - Aerial Conductor |  |  | 2 holes NEMA Pad
|  |  | - Creepage Distance |  |  | Approx. 387 | [7 empty] | mm
|  |  | - Applied Standard |  |  | As per IEEE 48 Standard
u. | Total Weight With Oil |  |  |  |  | Approx. 2650 | [7 empty] | kg
v. | Weight of Oil |  |  |  |  | Approx. 440 | [7 empty] | kg
w. | Volume of Oil |  |  |  |  | Approx. 490 | [7 empty] | Litres
x. | Overall Length ´ Width ´ Height |  |  |  |  | Approx. 2.07 x 1.99 x 1.90 | [7 empty] | m × m × m
y. | Mounting |  |  |  |  | Platform
z. | Dimension of Base |  |  |  |  | Approx. 0.70 x 0.77 | [7 empty] | m × m
Guaranteed Characteristics
| - No-load Loss at Rated Voltage and Frequency |  |  |  |  | 900 | [7 empty] | W
| - Load Loss at Rated Capacity, Voltage and |  |  |  |  | 5200 | [7 empty] | W
Frequency at 75 °C
| - Total Loss at Rated Capacity, Voltage and |  |  |  |  | 6100 | [7 empty] | W
Frequency at 75 °C
Important Notice:
The guaranteed characteristics shall be evaluated and included in the bid price for cost evaluation with the rate of
190 baht for each W or part thereof of the guaranteed no-load loss.
69 baht for each W or part thereof of the guaranteed load loss.
If the transformer fail to meet the guaranteed characteristics herein indicated, the price of transformers shall be reduced in accordance with the condition specified in Article : Penalty for Equipment not Meeting Guaranteed Characteristics.
Remark

## AB2_DX0403-Tirathai (hidden)
DISTRIBUTION TRANSFORMER
FORM PD 111,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB2
BIDDER |  | IN CONSORTIUM |  |  |  | ITEM NO. |  |  | 1AB2-2
a. | Manufacturer / Country |  |  |  |  | Tirathai Public Co.,Ltd./Thailand
b. | Type |  |  |  |  | 3 Ph, Outdoor oil immersed distribution Tr.
c. | Applied Standards |  |  |  |  | IEEE C57.12, TIS 384
d. | Max. Continuous Rated Capacity |  |  |  |  | 150 | [7 empty] | kVA
e. | Rated Voltage |  | - HV / LV |  |  | 0.4 |  |  |  | 0.4 |  |  |  | kV
f. | Rated Current |  | - HV / LV |  |  | 216.5 |  |  |  | 216.5 |  |  |  | A
g. | Impedance Voltage at Rated Voltage,
| Current, Frequency and 75 °C |  |  |  |  | ≥ 4.0 | [7 empty] | %
h. | Basic Insulation Level (BIL) of Windings
|  |  | - HV Winding |  |  | 30 | [7 empty] | kV
|  |  | - LV Winding |  |  | 30 | [7 empty] | kV
|  |  | - Neutral |  |  | 30 | [7 empty] | kV
i. | Vector Group |  |  |  |  | Dyn1
j. | Polarity |  |  |  |  | Subtractive
k. | Off Load Tap Changer
|  |  | - Manufacturer / Country |  |  | N/A
|  |  | - Type / Model No. |  |  | N/A
|  |  | - Tapping Range |  |  | - |  |  | % on |  | - |  |  | Side
l. | Exciting Current in % of Full Load Current
| at 110 % / 100% / 90% / 80% Rated Voltage |  |  |  |  | 27.1 |  | 2.08 |  | 0.64 |  |  | 0.42 | %
m. | Efficiency with 0.9 Lagging Pf. Load
| at 110 % / 100% / 50% Load |  |  |  |  | 97.83 |  |  | 97.97 |  |  | 98.49 |  | %
n. | Max. Short Circuit Current which the Transformer
shall be able to withstand
|  | Symmetrical |  | - HV / LV Winding |  | 3.13 |  |  |  | 5.41 |  |  |  | kA rms
|  | Asymmetrical |  | - HV / LV Winding |  | 5.7 |  |  |  | 9.87 |  |  |  | kA peak
o. | Temperature Rise
|  | - Average Winding / Hottest Spot |  |  |  | 55 |  |  |  | 65 |  |  |  | °C
|  | - Insulating Oil |  |  |  | 55 | [7 empty] | °C
p. | Insulating Material
|  | Winding Insulation Paper |  |  | - Manufacturer | Miki / Japan
[5 empty] | - Temp. Class | A (105 C)
|  | Other Insulating Material |  |  | - Manufacturer | Weidmann / Switzerland
[5 empty] | - Temp. Class | A (105 C)
q. | Internal Gas Pressure Withstanding of Tank |  |  |  |  | 0.7 | [7 empty] | kg/cm2
r. | Insulating Oil |  | - Type |  |  |  | Uninhibited |  |  | X |  | Inhibited
|  |  | - Manufacturer |  |  | PSP / Thailand
|  |  | - Manufacturer Type |  |  | Transform Inh
|  |  | - Applied Standard |  |  | IEC60296
Remark
s. | Bushing |  |  |  |  | HV |  |  | LV |  |  | Neutral
|  |  | - Manufacturer |  |  | Tirathai/Thailand |  |  | Tirathai/Thailand |  |  | Tirathai/Thailand
|  |  | - Type (Condenser or Solid) |  |  | Solid |  |  | Solid |  |  | Solid
|  |  | - Model No. |  |  | 1 NF 250 |  |  | 1 NF 250 |  |  | 1 NF 250
|  |  | - BIL |  |  | 30 |  |  | 30 |  |  | 30 |  | kV
|  |  | - Power Freq. Withstand (Dry) |  |  | 10 |  |  | 10 |  |  | 10 |  | kV
|  |  | - Power Freq. Withstand (Wet) |  |  | 10 |  |  | 10 |  |  | 10 |  | kV
|  |  | - Rated Current |  |  | 250 |  |  | 250 |  |  | 250 |  | A
|  |  | - Creepage Distance |  |  | 60 |  |  | 60 |  |  | 60 |  | mm
t. | Cable Terminations
|  |  | - Manufacturer |  |  | 3M
|  |  | - Type / Model / Cat. No. |  |  | Outdoor (Cold Shrink) / QT-II 5652
|  |  | - Material of External Insulator |  |  | Silicone Rubber
|  |  | - Rated Voltage |  |  | Insulation Class 25kV | [7 empty] | kV
|  |  | - Current Rating |  |  | As per Standard | [7 empty] | A
|  |  | - BIL |  |  | 150 | [7 empty] | kV
|  |  | - Aerial Conductor |  |  | 2 holes NEMA Pad
|  |  | - Creepage Distance |  |  | Approx. 387 | [7 empty] | mm
|  |  | - Applied Standard |  |  | As per IEEE 48 Standard
u. | Total Weight With Oil |  |  |  |  | Approx. 1100 | [7 empty] | kg
v. | Weight of Oil |  |  |  |  | Approx. 180 | [7 empty] | kg
w. | Volume of Oil |  |  |  |  | Approx. 200 | [7 empty] | Litres
x. | Overall Length ´ Width ´ Height |  |  |  |  | Approx. 1.41 x 1.54 x 1.33 | [7 empty] | m × m × m
y. | Mounting |  |  |  |  | Platform
z. | Dimension of Base |  |  |  |  | Approx. 0.55 x 0.55 | [7 empty] | m × m
Guaranteed Characteristics
| - No-load Loss at Rated Voltage and Frequency |  |  |  |  | 450 | [7 empty] | W
| - Load Loss at Rated Capacity, Voltage and |  |  |  |  | 2350 | [7 empty] | W
Frequency at 75 °C
| - Total Loss at Rated Capacity, Voltage and |  |  |  |  | 2800 | [7 empty] | W
Frequency at 75 °C
Important Notice:
The guaranteed characteristics shall be evaluated and included in the bid price for cost evaluation with the rate of
190 baht for each W or part thereof of the guaranteed no-load loss.
69 baht for each W or part thereof of the guaranteed load loss.
If the transformer fail to meet the guaranteed characteristics herein indicated, the price of transformers shall be reduced in accordance with the condition specified in Article : Penalty for Equipment not Meeting Guaranteed Characteristics.
Remark

## AB4_SA 396kV-Siemens (hidden)
SURGE ARRESTER
FORM PD 392,393,394,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB4 , and 3AB4
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB4-1, and 3AB4-1
a. | Manufacturer / Country
|  | - For SA |  | Siemens Energy/ Germany
|  | - For Supporting Structure |  | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  | ZnO/3EP/3EP6 396-3PJ42-2XA1-Z
c. | Applied Standards |  |  | IEEE C62.11
d. | Class (Station or Distribution) |  |  | Station Class
e. | Arrester Voltage Rating |  |  | 396 |  |  |  | kVrms
f. | Duty Cycle Current |  |  | 15 |  |  |  | kA
g. | Arrester Insulation Withstand
|  | - For BIL / 1 Min Dry / 10 s Wet |  | 1550 | 1210 |  | 1100 | kV
h. | Rated Frequency |  |  | 50 |  |  |  | Hz
i. | Maximum Continuous Operating Voltage (MCOV) |  |  | 318 |  |  |  | kVrms
j. | Maximum Equivalent Front-of-wave |  |  | 1103 @20kA |  |  |  | kVcrest
Protective Level
k. | Maximum Switching Surge Protective Level |  |  | 819 @3kA |  |  |  | kVcrest
l. | Maximum Discharge Voltage at 5/ 10 / 20 kA |  |  | 865 | 920 |  | 1012 | kVcrest
m. | One Minute Energy Absorption Capability |  |  | 10 |  |  |  | kJ/kV
at Maximum L-G Voltage (45oC Ambient)
n. | Power Frequency Reference Voltage |  |  | 403,9…431,6 |  |  |  | kVrms
o. | Power Frequency Reference Current |  |  | 5,0 / 51,4 = 0,099 |  |  |  | mA peak/ cm2
p. | Leakage Current at
|  | - MCOV |  | ≤ 2,0 |  |  |  | mA
|  | - Nominal System L-G Voltage |  | ≤1,7 |  |  |  | mA
q. | RIV at 1.05 Max. System L-G Operating Voltage |  |  | ≤2500 |  |  |  | µV
r. | Creepage Distance of Insulator |  |  | 15336 |  |  |  | mm
s. | Insulator Color |  |  | porcelain brown
t. | Weight |  |  | 478 |  |  |  | kg
u. | Discharge Counter
|  | - Manufacturer / Country |  | Siemens Energy / China
|  | - Type / Model |  | Electromechanical/3EX5 050-0A
|  | - Minimum Impulse Registration |  | 200 |  |  |  | A
|  | - Registration Capability per Second |  | 5
|  | - Indicating Ammeter Scale |  | 0-10 |  |  |  | mA peak
Remark

## AB4_SA 192kV-Siemens (hidden)
SURGE ARRESTER
FORM PD 392,393,394,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 2AB4
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 2AB4-1
a. | Manufacturer / Country
|  | - For SA |  | Siemens Energy/ Germany
|  | - For Supporting Structure |  | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  | ZnO/3EP/3EP4 192-2PE32-1XA1-Z
c. | Applied Standards |  |  | IEEE C62.11 (2012)
d. | Class (Station or Distribution) |  |  | Station Class
e. | Arrester Voltage Rating |  |  | 192 |  |  |  | kVrms
f. | Duty Cycle Current |  |  | 10 |  |  |  | kA
g. | Arrester Insulation Withstand
|  | - For BIL / 1 Min Dry / 10 s Wet |  | 900 | 465 |  | 385 | kV
h. | Rated Frequency |  |  | 50 |  |  |  | Hz
i. | Maximum Continuous Operating Voltage (MCOV) |  |  | 152 |  |  |  | kVrms
j. | Maximum Equivalent Front-of-wave |  |  | 485 |  |  |  | kVcrest
Protective Level
k. | Maximum Switching Surge Protective Level |  |  | 379 |  |  |  | kVcrest
l. | Maximum Discharge Voltage at 5/ 10 / 20 kA |  |  | 415 | 441 |  | 490 | kVcrest
m. | One Minute Energy Absorption Capability |  |  | 4,0 |  |  |  | kJ/kV
at Maximum L-G Voltage (45oC Ambient)
n. | Power Frequency Reference Voltage |  |  | 192,0…207,4 |  |  |  | kVrms
o. | Power Frequency Reference Current |  |  | 3,0 / 26.42 = 0,114 |  |  |  | mA peak/ cm2
p. | Leakage Current at
|  | - MCOV |  | ≤ 1,5 |  |  |  | mA
|  | - Nominal System L-G Voltage |  | ≤ 1,2 |  |  |  | mA
q. | RIV at 1.05 Max. System L-G Operating Voltage |  |  | ≤ 200 (PD LEVEL < 10 pC) |  |  |  | µV
r. | Creepage Distance of Insulator |  |  | 6810 |  |  |  | mm
s. | Insulator Color |  |  | Poreclain brown
t. | Weight |  |  | ~140 |  |  |  | kg
u. | Discharge Counter
|  | - Manufacturer / Country |  | SIEMENS Energy/ China
|  | - Type / Model |  | Electromechanical /3EX5 050-0A
|  | - Minimum Impulse Registration |  | 200 |  |  |  | A
|  | - Registration Capability per Second |  | 5
|  | - Indicating Ammeter Scale |  | 0~10 |  |  |  | mA peak
Remark

## AB5_CT 230kV-Arteche (hidden)
CURRENT TRANSFORMER
FORM PD 301.1, 306, 1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 4AB5
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 4AB5-1
a. | Manufacturer / Country
|  | - For CT |  |  | ARTECHE / SPAIN
|  | - For Supporting Structure |  |  | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | CA-245
c. | Applied Standards |  |  |  | IEEE Std C57.13
d. | Rated Voltage / Frequency |  |  |  | 230 |  | kV / | 50 |  |  | Hz
e. | Rated Current - Primary / Secondary |  |  |  | 4000 |  | A / | 1 |  |  | A
f. | Number of Turns - Primary / Secondary |  |  |  | 1 |  | Turns / |  | 4000 |  |  | Turns
g. | Maximum Service Voltage |  |  |  | 245 | [7 empty] | kV
h. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet |  | 460 |  | kV / | 460 |  |  | kV
|  |  | - BIL / BSL |  | 1050 |  | kV / | - |  |  | kV
i. | Insulator |  | - Creepage Distance |  | >=6125 | [7 empty] | mm
|  |  | - Color |  | Brown
|  |  | - Cemented Flange Type |  | X | Yes |  |  |  | No
j. | Current Ratio |  | - Core No. 1 |  | 500/1000/1500/2000/2500/3000/3500/4000:1A
|  |  | - Core No. 2 |  | 500/1000/1500/2000/2500/3000/3500/4000:1A
|  |  | - Core No. 3 |  | 500/1000/1500/2000/2500/3000/3500/4000:1A
|  |  | - Core No. 4 |  | 500/1000/1500/2000/2500/3000/3500/4000:1A
|  |  | - Core No. 5 |  | 500/1000/1500/2000/2500/3000/3500/4000:1A
- Core No. 6
k. | Accuracy Class |  | - Core No. 1 |  | C800
|  |  | - Core No. 2 |  | C800
|  |  | - Core No. 3 |  | C800
|  |  | - Core No. 4 |  | C800
|  |  | - Core No. 5 |  | C800
- Core No. 6
l. | Continuous Thermal Current Rating Factor |  |  |  | 1
m. | Ith (Thermal for 1 Sec.) / Idyn (Mechanical) |  |  |  | 63 |  | kA rms / |  | 158 |  |  | kA peak
n. | Primary Protective Device |  |  |  |  | With |  |  | X | Without
o. | Core |  | - Flux Density at Rated Burden | [9 empty] | Tesla
|  |  | - Cross Section Area of Core | [9 empty] | mm2
|  |  | - Location |  | X | Top |  |  |  | Bottom
|  |  | - Type of Core |  | X | Non Gapped |  |  |  | Gapped
p. | Oil Expansion System
|  |  | - Type |  | X | Bellow |  |  |  | N2 Cushion
Other
|  |  | - Material of Bellow |  | X | Metallic |  |  |  | Rubber
Other
q. | Total Weight / Volume of Oil |  |  |  | ~480/146 | [7 empty] | kg / Litres
Remark

## AB5_CT 22kV-Precise (hidden)
CURRENT TRANSFORMER
FORM PD 301.1, 306, 1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB5
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB5-1
a. | Manufacturer / Country
|  | - For CT |  |  | Precise Electric Manufacturing Co.,Ltd. / Thailand
|  | - For Supporting Structure |  |  | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | Outdoor, Oil filled/COU-36 /COU-36
c. | Applied Standards |  |  |  | IEEE Std.C57.13
d. | Rated Voltage / Frequency |  |  |  | 22 |  | kV / | 50 |  |  | Hz
e. | Rated Current - Primary / Secondary |  |  |  | 1800 |  | A / | Tap1-2:0.9A,Tap2-3:0.45A,Tap1-3:0.3A |  |  | A
f. | Number of Turns - Primary / Secondary |  |  |  | 1 |  | Turns / |  | 6000 |  |  | Turns
g. | Maximum Service Voltage |  |  |  | 24 | [7 empty] | kV
h. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet |  | 50 |  | kV / | 50 |  |  | kV
|  |  | - BIL / BSL |  | 150 |  | kV / | - |  |  | kV
i. | Insulator |  | - Creepage Distance |  | 930 - 960 | [7 empty] | mm
|  |  | - Color |  | Chocolate Brown
|  |  | - Cemented Flange Type |  | X | Yes |  |  |  | No
j. | Current Ratio |  | - Core No. 1 |  | 2000/4000/6000:1
|  |  | - Core No. 2 |  | 2000/4000/6000:1
|  |  | - Core No. 3 |  | 2000/4000/6000:1
|  |  | - Core No. 4 |  | -
|  |  | - Core No. 5 |  | -
|  |  | - Core No. 6 |  | -
k. | Accuracy Class |  | - Core No. 1 |  | C1000
|  |  | - Core No. 2 |  | C1000
|  |  | - Core No. 3 |  | C1000
|  |  | - Core No. 4 |  | -
|  |  | - Core No. 5 |  | -
|  |  | - Core No. 6 |  | -
l. | Continuous Thermal Current Rating Factor |  |  |  | 1.0
m. | Ith (Thermal for 1 Sec.) / Idyn (Mechanical) |  |  |  | 13 |  | kA rms / |  | 35 |  |  | kA peak
n. | Primary Protective Device |  |  |  |  | With |  |  | X | Without
o. | Core |  | - Flux Density at Rated Burden |  | 0.085 | [7 empty] | Tesla
|  |  | - Cross Section Area of Core |  | 960 | [7 empty] | mm2
|  |  | - Location |  |  | Top |  |  | X | Bottom
|  |  | - Type of Core |  | X | Non Gapped |  |  |  | Gapped
p. | Oil Expansion System
|  |  | - Type |  | X | Bellow |  |  |  | N2 Cushion
Other
|  |  | - Material of Bellow |  | X | Metallic |  |  |  | Rubber
Other
q. | Total Weight / Volume of Oil |  |  |  | 220 / 22 | [7 empty] | kg / Litres
Remark

## AB6_CCVT 525kV-Arteche (PD9011) (hidden)
COUPLING CAPACITOR VOLTAGE TRANSFORMER
FORM PD 301.2,305,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  |  | 1AB6-2
a. | Manufacturer / Country |  |  | - For CCVT | Electrotecnica Arteche Hermanos S.L. / SPAIN
|  |  |  | - For Supporting Structure | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | DFK-525
c. | Applied Standards |  |  |  | ANSI C93.1
d. | Rated Voltage / Frequency |  |  |  | 525 |  |  | kV | 50 |  |  | Hz
e. | Maximum Service Voltage |  |  |  | 550 | [6 empty] | kV
f. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet (50 Hz) |  | 785 |  |  | kV | 785 |  |  | kV
|  |  | - BIL / BSL |  | 1550 |  |  | kV | - |  |  | kV
g. | Insulator |  | - Creepage Distance / Color |  | >=13750 |  |  |  | mm |  | Brown
|  |  | - Cement Flange Type |  | X | Yes |  |  |  |  | No
h. | Voltage Ratio |  |  |  | 2500/4500 & 2500/4500 & 2500/4500:1
i. | Secondary Voltage Rating (Base on Nominal System Voltage)
|  | - No.1 Secondary Winding |  |  | 115/63.9 | [6 empty] | V
|  | - No.2 Secondary Winding |  |  | 115/63.9 | [6 empty] | V
|  | - No.3 Secondary Winding |  |  | 115/63.9 | [6 empty] | V
|  | - No.4 Secondary Winding | [9 empty] | V
j. | Burden
|  | - No.1 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.2 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.3 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.4 Secondary Winding | [9 empty] | VA
|  | - Simultaneous / Thermal |  |  | 75 |  |  | VA | 1000 |  |  | VA
k. | Accuracy Class
|  | - No.1 Secondary Winding |  |  | 1.2R WXY
|  | - No.2 Secondary Winding |  |  | 1.2R WXY
|  | - No.3 Secondary Winding |  |  | 1.2R WXY
- No.4 Secondary Winding
l. | Capacitance |  | - C1 / C2 |  | 6622 |  |  | pF | 141606 |  |  | pF
|  |  | - Rated |  | ~6200 | [6 empty] | pF
m. | Primary Voltage Rating of Intermediate Transformer |  |  |  | 22/√3 | [6 empty] | kV
n. | Potential Grounding Switch |  |  |  | X | With |  |  |  |  | Without
o. | Available Short Circuit Current at Each Secondary Tapping
|  | - No.1 Secondary Winding |  |  | 66 |  |  | A | 120 |  |  | A
|  | - No.2 Secondary Winding |  |  | 66 |  |  | A | 120 |  |  | A
|  | - No.3 Secondary Winding |  |  | 66 |  |  | A | 120 |  |  | A
|  | - No.4 Secondary Winding | [5 empty] | A |  |  |  | A
p. | Oil Expansion System
|  |  | - Type |  | X | Bellow |  |  |  |  | N2 Cushion
Other
|  |  | - Material of Bellow |  | X | Metallic |  |  |  |  | Rubber
Other
Remark
q. | Ferroresonance Suppression Device |  |  |  |  | Electronic
[5 empty] | X | Resistive and/or Reactive Element
r. | Carrier Drain Coil
|  | - Impulse Withstand Voltage | [9 empty] | kV
|  | - Frequency Range | [9 empty] | kHz
|  | - Insertion Loss at Specified Freq. Range | [9 empty] | dB
|  | - Voltage Drop at 50 Hz | [9 empty] | V
|  | - Inductance of Carrier Drain Coil | [9 empty] | mH
|  | - Impedance at Specified Freq. Range | [9 empty] | Kilo-Ohms
|  | - Impedance at 50 Hz | [9 empty] | Ohms
|  | - Continuous/Short Time Current/Duration |  |  |  |  | A/ |  |  | A/ |  | s
|  | - Protective Gap Setting | [6 empty] | mm |  |  | kV
s. | Total Weight | [10 empty] | kg
t. | Volume of Oil | [10 empty] | Litres
Remark

## AB6_CCVT 525kV-Arteche (PD9W11) (hidden)
COUPLING CAPACITOR VOLTAGE TRANSFORMER
FORM PD 301.2,305,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 1AB6, 3AB6
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  |  | 1AB6-1, 3AB6-1
a. | Manufacturer / Country |  |  | - For CCVT | Electrotecnica Arteche Hermanos S.L. / SPAIN
|  |  |  | - For Supporting Structure | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | DFK-525
c. | Applied Standards |  |  |  | ANSI C93.1
d. | Rated Voltage / Frequency |  |  |  | 525 |  |  | kV | 50 |  |  | Hz
e. | Maximum Service Voltage |  |  |  | 550 | [6 empty] | kV
f. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet (50 Hz) |  | 785 |  |  | kV | 785 |  |  | kV
|  |  | - BIL / BSL |  | 1550 |  |  | kV | - |  |  | kV
g. | Insulator |  | - Creepage Distance / Color |  | >=13750 |  |  |  | mm |  | Brown
|  |  | - Cement Flange Type |  | X | Yes |  |  |  |  | No
h. | Voltage Ratio |  |  |  | 2500/4500 & 2500/4500 & 2500/4500:1
i. | Secondary Voltage Rating (Base on Nominal System Voltage)
|  | - No.1 Secondary Winding |  |  | 115/63.9 | [6 empty] | V
|  | - No.2 Secondary Winding |  |  | 115/63.9 | [6 empty] | V
|  | - No.3 Secondary Winding |  |  | 115/63.9 | [6 empty] | V
|  | - No.4 Secondary Winding | [9 empty] | V
j. | Burden
|  | - No.1 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.2 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.3 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.4 Secondary Winding | [9 empty] | VA
|  | - Simultaneous / Thermal |  |  | 75 |  |  | VA | 1000 |  |  | VA
k. | Accuracy Class
|  | - No.1 Secondary Winding |  |  | 1.2R WXY
|  | - No.2 Secondary Winding |  |  | 1.2R WXY
|  | - No.3 Secondary Winding |  |  | 1.2R WXY
- No.4 Secondary Winding
l. | Capacitance |  | - C1 / C2 |  | 6622 |  |  | pF | 141606 |  |  | pF
|  |  | - Rated |  | ~6200 | [6 empty] | pF
m. | Primary Voltage Rating of Intermediate Transformer |  |  |  | 22/√3 | [6 empty] | kV
n. | Potential Grounding Switch |  |  |  | X | With |  |  |  |  | Without
o. | Available Short Circuit Current at Each Secondary Tapping
|  | - No.1 Secondary Winding |  |  | 66 |  |  | A | 120 |  |  | A
|  | - No.2 Secondary Winding |  |  | 66 |  |  | A | 120 |  |  | A
|  | - No.3 Secondary Winding |  |  | 66 |  |  | A | 120 |  |  | A
|  | - No.4 Secondary Winding | [5 empty] | A |  |  |  | A
p. | Oil Expansion System
|  |  | - Type |  | X | Bellow |  |  |  |  | N2 Cushion
Other
|  |  | - Material of Bellow |  | X | Metallic |  |  |  |  | Rubber
Other
Remark
q. | Ferroresonance Suppression Device |  |  |  |  | Electronic
[5 empty] | X | Resistive and/or Reactive Element
r. | Carrier Drain Coil
|  | - Impulse Withstand Voltage |  |  | 15 | [6 empty] | kV
|  | - Frequency Range |  |  | 70-450 | [6 empty] | kHz
|  | - Insertion Loss at Specified Freq. Range |  |  | <0.5 | [6 empty] | dB
|  | - Voltage Drop at 50 Hz |  |  | <30 | [6 empty] | V
|  | - Inductance of Carrier Drain Coil |  |  | 42 | [6 empty] | mH
|  | - Impedance at Specified Freq. Range |  |  | -10-125 | [6 empty] | Kilo-Ohms
|  | - Impedance at 50 Hz |  |  | 12.3 | [6 empty] | Ohms
|  | - Continuous/Short Time Current/Duration |  |  | 1 |  | A/ | 50 |  | A/ | 0.2 | s
|  | - Protective Gap Setting |  |  | - |  |  |  | mm |  | - | kV
s. | Total Weight |  |  |  | 1065 | [6 empty] | kg
t. | Volume of Oil |  |  |  | ~168 | [6 empty] | Litres
Remark

## AB6_CCVT 230kV-Arteche (PDW81J) (hidden)
COUPLING CAPACITOR VOLTAGE TRANSFORMER
FORM PD 301.2,305,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 4AB6
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  |  | 4AB6-1
a. | Manufacturer / Country |  |  | - For CCVT | ELECTROTECNICA ARTECHE HERMANOS S.L.,/SPAIN
|  |  |  | - For Supporting Structure | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | DFK-245
c. | Applied Standards |  |  |  | ANSI C93.1
d. | Rated Voltage / Frequency |  |  |  | 230 |  |  | kV | 50 |  |  | Hz
e. | Maximum Service Voltage |  |  |  | 242 | [6 empty] | kV
f. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet (50 Hz) |  | 460 |  |  | kV | 395 |  |  | kV
|  |  | - BIL / BSL |  | 900 |  |  | kV | - |  |  | kV
g. | Insulator |  | - Creepage Distance / Color |  | >=6050 |  |  |  | mm |  | Brown
|  |  | - Cement Flange Type |  | X | Yes |  |  |  |  | No
h. | Voltage Ratio |  |  |  | 1155/2000 & 1155/2000:1
i. | Secondary Voltage Rating (Base on Nominal System Voltage)
|  | - No.1 Secondary Winding |  |  | 119,5/69 | [6 empty] | V
|  | - No.2 Secondary Winding |  |  | 119,5/69 | [6 empty] | V
|  | - No.3 Secondary Winding | [9 empty] | V
|  | - No.4 Secondary Winding | [9 empty] | V
j. | Burden
|  | - No.1 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.2 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.3 Secondary Winding | [9 empty] | VA
|  | - No.4 Secondary Winding | [9 empty] | VA
|  | - Simultaneous / Thermal |  |  | 75 |  |  | VA | 600 |  |  | VA
k. | Accuracy Class
|  | - No.1 Secondary Winding |  |  | 1.2R WXY
|  | - No.2 Secondary Winding |  |  | 1.2R WXY
- No.3 Secondary Winding
- No.4 Secondary Winding
l. | Capacitance |  | - C1 / C2 |  | ~3,108 |  |  | pF | ~27,969 |  |  | pF
|  |  | - Rated |  | ~2800pF +10/-5% | [6 empty] | pF
m. | Primary Voltage Rating of Intermediate Transformer |  |  |  | ~22/v3 +-10% | [6 empty] | kV
n. | Potential Grounding Switch |  |  |  | X | With |  |  |  |  | Without
o. | Available Short Circuit Current at Each Secondary Tapping
|  | - No.1 Secondary Winding |  |  | 15 |  |  | A | 25 |  |  | A
|  | - No.2 Secondary Winding |  |  | 15 |  |  | A | 25 |  |  | A
|  | - No.3 Secondary Winding | [5 empty] | A |  |  |  | A
|  | - No.4 Secondary Winding | [5 empty] | A |  |  |  | A
p. | Oil Expansion System
|  |  | - Type |  | X | Bellow |  |  |  |  | N2 Cushion
Other
|  |  | - Material of Bellow |  | X | Metallic |  |  |  |  | Rubber
Other
Remark
q. | Ferroresonance Suppression Device |  |  |  |  | Electronic
[5 empty] | X | Resistive and/or Reactive Element
r. | Carrier Drain Coil
|  | - Impulse Withstand Voltage |  |  | 12 | [6 empty] | kV
|  | - Frequency Range |  |  | 70-450 | [6 empty] | kHz
|  | - Insertion Loss at Specified Freq. Range |  |  | <0.5 | [6 empty] | dB
|  | - Voltage Drop at 50 Hz |  |  | <30 | [6 empty] | V
|  | - Inductance of Carrier Drain Coil |  |  | 12 | [6 empty] | mH
|  | - Impedance at Specified Freq. Range |  |  | ~10-125 | [6 empty] | Kilo-Ohms
|  | - Impedance at 50 Hz |  |  | 12.6 | [6 empty] | Ohms
|  | - Continuous/Short Time Current/Duration |  |  | 1 |  | A/ | 50 |  | A/ | 0.2 | s
|  | - Protective Gap Setting |  |  | - |  |  |  | mm |  | - | kV
s. | Total Weight |  |  |  | ~410 | [6 empty] | kg
t. | Volume of Oil |  |  |  | ~56 | [6 empty] | Litres
Remark

## AB6_CCVT 230kV-Emek (hidden)
COUPLING CAPACITOR VOLTAGE TRANSFORMER
FORM PD 301.2,305,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 4AB6
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  |  | 4AB6-1
a. | Manufacturer / Country |  |  | - For CCVT | EMEK / TURKEY
|  |  |  | - For Supporting Structure | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | Outdoor, Oil Filled / KGT-245
c. | Applied Standards |  |  |  | ANSI C93.1
d. | Rated Voltage / Frequency |  |  |  | 230 |  |  | kV | 50 |  |  | Hz
e. | Maximum Service Voltage |  |  |  | 242 | [6 empty] | kV
f. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet (50 Hz) |  | 525 |  |  | kV | 460 |  |  | kV
|  |  | - BIL / BSL |  | 1050 |  |  | kV |  |  |  | kV
g. | Insulator |  | - Creepage Distance / Color |  | ≥6050 |  |  |  | mm |  | Brown
|  |  | - Cement Flange Type |  | X | Yes |  |  |  |  | No
h. | Voltage Ratio |  |  |  | 1155/2000 & 1155/2000:1
i. | Secondary Voltage Rating (Base on Nominal System Voltage)
|  | - No.1 Secondary Winding |  |  | 119,5 / 69 | [6 empty] | V
|  | - No.2 Secondary Winding |  |  | 119,5 / 69 | [6 empty] | V
|  | - No.3 Secondary Winding | [9 empty] | V
|  | - No.4 Secondary Winding | [9 empty] | V
j. | Burden
|  | - No.1 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.2 Secondary Winding |  |  | 75 | [6 empty] | VA
|  | - No.3 Secondary Winding | [9 empty] | VA
|  | - No.4 Secondary Winding | [9 empty] | VA
|  | - Simultaneous / Thermal |  |  | 75 |  |  | VA | 1000 |  |  | VA
k. | Accuracy Class
|  | - No.1 Secondary Winding |  |  | 1,2R WXY
|  | - No.2 Secondary Winding |  |  | 1,2R WXY
- No.3 Secondary Winding
- No.4 Secondary Winding
l. | Capacitance |  | - C1 / C2 |  | 4303 |  |  | pF | 56727 |  |  | pF
|  |  | - Rated |  | 4000 | [6 empty] | pF
m. | Primary Voltage Rating of Intermediate Transformer |  |  |  | ~16,85/V3 | [6 empty] | kV
n. | Potential Grounding Switch |  |  |  | X | With |  |  |  |  | Without
o. | Available Short Circuit Current at Each Secondary Tapping
|  | - No.1 Secondary Winding |  |  | X1-X3: ~99 |  |  | A | X2-X3: ~165 |  |  | A
|  | - No.2 Secondary Winding |  |  | Y1-Y3: ~99 |  |  | A | Y2-Y3: ~165 |  |  | A
|  | - No.3 Secondary Winding | [5 empty] | A |  |  |  | A
|  | - No.4 Secondary Winding | [5 empty] | A |  |  |  | A
p. | Oil Expansion System
|  |  | - Type |  | X | Bellow |  |  |  |  | N2 Cushion
Other
|  |  | - Material of Bellow |  | X | Metallic |  |  |  |  | Rubber
Other
Remark
q. | Ferroresonance Suppression Device |  |  |  |  | Electronic
[5 empty] | X | Resistive and/or Reactive Element
r. | Carrier Drain Coil
|  | - Impulse Withstand Voltage | [9 empty] | kV
|  | - Frequency Range | [9 empty] | kHz
|  | - Insertion Loss at Specified Freq. Range | [9 empty] | dB
|  | - Voltage Drop at 50 Hz | [9 empty] | V
|  | - Inductance of Carrier Drain Coil | [9 empty] | mH
|  | - Impedance at Specified Freq. Range | [9 empty] | Kilo-Ohms
|  | - Impedance at 50 Hz | [9 empty] | Ohms
|  | - Continuous/Short Time Current/Duration |  |  |  |  | A/ |  |  | A/ |  | s
|  | - Protective Gap Setting | [6 empty] | mm |  |  | kV
s. | Total Weight |  |  |  | 600 | [6 empty] | kg
t. | Volume of Oil |  |  |  | ~75 in EMU ~25 in cap. | [6 empty] | Litres
Remark

## AB6_VT 22kV- Precise (hidden)
VOLTAGE TRANSFORMER
FORM PD 301.3, 1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  |  | 1AB6-3
a. | Manufacturer / Country
|  |  | - For VT |  | Precise Electric Manufacturing Co.,Ltd. / Thailand
|  |  | - For Supporting Structure |  | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | Outdoor, Oilfilled/VOG-24/VOG12-36
c. | Applied Standards |  |  |  | IEC 61869-3
d. | Rated Voltage / Frequency |  |  |  | 22/√3 |  |  | kV/ | 50 |  |  | Hz
e. | Maximum Service Voltage |  |  |  | 24 | [7 empty] | kV
f. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet (50 Hz) |  | 50 |  |  | kV/ | 50 |  |  | kV
|  |  | - BIL / BSL |  | 150 |  |  | kV/ | - |  |  | kV
g. | Insulator | - Creepage Distance |  |  | 940 - 1040 | [7 empty] | mm
|  | - Color |  |  | Chocolate Brown
|  | - Cemented Flange Type |  |  | X | Yes |  |  |  | No
h. | Voltage Ratio |  |  |  | 200&200:1
i. | Secondary Voltage Rating (Base on Nominal System Voltage)
|  | - No.1 Secondary Winding |  |  | 110/√3 | [7 empty] | V
|  | - No.2 Secondary Winding |  |  | 110/√3 | [7 empty] | V
|  | - No.3 Secondary Winding |  |  | - | [7 empty] | V*
j. | Burden
|  | - No.1 Secondary Winding |  |  | 50 | [7 empty] | VA
|  | - No.2 Secondary Winding |  |  | 50 | [7 empty] | VA
|  | - No.3 Secondary Winding |  |  | - | [7 empty] | VA*
|  | - Simultaneous |  |  | 50 | [7 empty] | VA
|  | - Thermal of No.1/2/3 Secondary Winding |  |  | 500 |  | VA/ | 500 |  | VA/ |  | - | VA
k. | Accuracy Class
|  | - No.1 Secondary Winding |  |  | 0.2
|  | - No.2 Secondary Winding |  |  | 0.2
|  | - No.3 Secondary Winding |  |  | -
l. | Total Weight |  |  |  | 90 | [7 empty] | kg
m. | Volume of Oil |  |  |  | 14 | [7 empty] | Litres
Note: |  | *Secondary winding for ferroresonance suppression (for reference).
Information of the ferroresonance suppression shall be submitted for consideration.
Remark

## AB6_VT - Emek (hidden)
VOLTAGE TRANSFORMER
FORM PD 301.3, 1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  |  | 1AB6-3
a. | Manufacturer / Country
|  |  | - For VT |  | EMEK / TURKEY
|  |  | - For Supporting Structure |  | AJIKAWA & SCI OR SKY TOWER OR SST
b. | Type / Model / Catalog No. |  |  |  | GT1-24
c. | Applied Standards |  |  |  | IEC 61869-1 and IEC61869-3
d. | Rated Voltage / Frequency |  |  |  | 22 |  |  | kV/ | 50 |  |  | Hz
e. | Maximum Service Voltage |  |  |  | 24 | [7 empty] | kV
f. | Insulation Level |  | - 1 Min. Dry / 10 Sec. Wet (50 Hz) |  | 50 |  |  | kV/ | 50 |  |  | kV
|  |  | - BIL / BSL |  | 150 |  |  | kV/ |  |  |  | kV
g. | Insulator | - Creepage Distance |  |  | ≥600 | [7 empty] | mm
|  | - Color |  |  | Brown porcelian
|  | - Cemented Flange Type |  |  | X | Yes |  |  |  | No
h. | Voltage Ratio |  |  |  | 200&200:1
i. | Secondary Voltage Rating (Base on Nominal System Voltage)
|  | - No.1 Secondary Winding |  |  | 110/V3 | [7 empty] | V
|  | - No.2 Secondary Winding |  |  | 110/V3 | [7 empty] | V
|  | - No.3 Secondary Winding | [10 empty] | V*
j. | Burden
|  | - No.1 Secondary Winding |  |  | 50 | [7 empty] | VA
|  | - No.2 Secondary Winding |  |  | 50 | [7 empty] | VA
|  | - No.3 Secondary Winding | [10 empty] | VA*
|  | - Simultaneous |  |  | 50 | [7 empty] | VA
|  | - Thermal of No.1/2/3 Secondary Winding |  |  | 500 |  | VA/ | 500 |  | VA/ |  |  | VA
k. | Accuracy Class
|  | - No.1 Secondary Winding |  |  | 0.2
|  | - No.2 Secondary Winding |  |  | 0.2
- No.3 Secondary Winding
l. | Total Weight |  |  |  | 250 ±10% | [7 empty] | kg
m. | Volume of Oil |  |  |  | 60 | [7 empty] | Litres
Note: |  | *Secondary winding for ferroresonance suppression (for reference).
Information of the ferroresonance suppression shall be submitted for consideration.
Remark

## 1AB5-2_CT7-Precise (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 1AB5
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  |  | 1AB5-2
a. | Manufacturer / Country |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Type of Core |  |  | X | CT | 7 |  | PT |  |  |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | FUJI / Japan
| - Type / Model / Catalogue No. |  |  | TU-ST
| - Rating |  |  | 600 |  |  | V | 40 |  |  |  |  | A
| - Material |  |  | Non-Flammable , Thermosetting
| - Short-Circuit Type |  |  | X | Yes |  |  |  |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | -
| - Type / Model / Catalogue No. |  |  | -
| - Rating |  |  | - |  |  | V | - |  |  |  |  | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | -
e. | Paint
| - Manufacturer / Country |  |  | Cornel / Thailand
| - Type |  |  | Weather Resistant Serial PE Semi-Gloss
| - Color |  |  | Munsell 7.5 BG 6/15
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 1AB6-6_PT7-Precise (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB6-6
a. | Manufacturer / Country |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 7 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 600 |  | V | 75 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermosetting
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | LS / Korea , SCHNEIDER / Germany
| - Type / Model / Catalogue No. |  |  | BKN-b 1PC3A / BKN-b 3PC3A / A9F74370
| - Rating |  |  | 240/415 |  | V | 3, 3, 0.5 | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | AX , iOF
e. | Paint
| - Manufacturer / Country |  |  | Cornel / Thailand
| - Type |  |  | Weather Resistant Serial PE Semi-Gloss
| - Color |  |  | Munsell 7.5 BG 6/15
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 1AB6-7_PT8-Precise (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB6-7
a. | Manufacturer / Country |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 8 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 600 |  | V | 75 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermosetting
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | LS / Korea
| - Type / Model / Catalogue No. |  |  | BKN-b 1PC3A
| - Rating |  |  | 240 |  | V | 3 | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | AX
e. | Paint
| - Manufacturer / Country |  |  | Cornel / Thailand
| - Type |  |  | Weather Resistant Serial PE Semi-Gloss
| - Color |  |  | Munsell 7.5 BG 6/15
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 1AB6-8_PT6-Precise (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB6-8
a. | Manufacturer / Country |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 6 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 600 |  | V | 75 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermosetting
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | LS / Korea
| - Type / Model / Catalogue No. |  |  | BKN-b 3PC6A
| - Rating |  |  | 415 |  | V | 6 | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | AX
e. | Paint
| - Manufacturer / Country |  |  | Cornel / Thailand
| - Type |  |  | Weather Resistant Serial PE Semi-Gloss
| - Color |  |  | Munsell 7.5 BG 6/15
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 3AB6-3_PT7-Precise (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 3AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 3AB6-3
a. | Manufacturer / Country |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 7 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 600 |  | V | 75 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermosetting
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | LS / Korea , SCHNEIDER / Germany
| - Type / Model / Catalogue No. |  |  | BKN-b 1PC3A / BKN-b 3PC3A / A9F74370
| - Rating |  |  | 240/415 |  | V | 3, 3, 0.5 | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | AX , iOF
e. | Paint
| - Manufacturer / Country |  |  | Cornel / Thailand
| - Type |  |  | Weather Resistant Serial PE Semi-Gloss
| - Color |  |  | Munsell 7.5 BG 6/15
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 4AB5-3_CT6-Precise (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 4AB5
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  |  | 4AB5-3
a. | Manufacturer / Country |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Type of Core |  |  | X | CT | 6 |  | PT |  |  |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | FUJI / Japan
| - Type / Model / Catalogue No. |  |  | TU-ST
| - Rating |  |  | 600 |  |  | V | 40 |  |  |  |  | A
| - Material |  |  | Non-Flammable , Thermosetting
| - Short-Circuit Type |  |  | X | Yes |  |  |  |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | -
| - Type / Model / Catalogue No. |  |  | -
| - Rating |  |  | - |  |  | V | - |  |  |  |  | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | -
e. | Paint
| - Manufacturer / Country |  |  | Cornel / Thailand
| - Type |  |  | Weather Resistant Serial PE Semi-Gloss
| - Color |  |  | Munsell 7.5 BG 6/15
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 4AB6-3_PT11-Precise (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 4AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 4AB6-3
a. | Manufacturer / Country |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 11 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 600 |  | V | 75 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermosetting
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | LS / Korea , SCHNEIDER / Germany
| - Type / Model / Catalogue No. |  |  | BKN-b 1PC3A / BKN-b 3PC3A / A9F74370
| - Rating |  |  | 240/415 |  | V | 3, 3, 0.5 | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | AX , iOF
e. | Paint
| - Manufacturer / Country |  |  | Cornel / Thailand
| - Type |  |  | Weather Resistant Serial PE Semi-Gloss
| - Color |  |  | Munsell 7.5 BG 6/15
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 1AB5-2_SCI (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 1AB5
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  |  | 1AB5-2
a. | Manufacturer / Country |  |  | SCI Electric PCL/Thailand
b. | Type / Type of Core |  |  | X | CT | 7 |  | PT |  |  |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | FUJI Electric / Japan
| - Type / Model / Catalogue No. |  |  | TU-ST
| - Rating |  |  | 600 |  |  | V | 40 |  |  |  |  | A
| - Material |  |  | Non-Flammable , Thermoplastic
| - Short-Circuit Type |  |  | X | Yes |  |  |  |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
- Manufacturer / Country
- Type / Model / Catalogue No.
| - Rating | [5 empty] | V | [5 empty] | A
- Auxiliary Switch
- Type / Model / Catalogue No.
e. | Paint
| - Manufacturer / Country |  |  | Powder Plus/Thailand
| - Type |  |  | Polyester TGIC
| - Color |  |  | Munsell 7.5 BG 6/1.5
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 4AB5-3_SCI (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  |  | 4AB5
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  |  | 4AB5-3
a. | Manufacturer / Country |  |  | SCI Electric PCL/Thailand
b. | Type / Type of Core |  |  | X | CT | 6 |  | PT |  |  |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | FUJI Electric / Japan
| - Type / Model / Catalogue No. |  |  | TU-ST
| - Rating |  |  | 600 |  |  | V | 40 |  |  |  |  | A
| - Material |  |  | Non-Flammable , Thermoplastic
| - Short-Circuit Type |  |  | X | Yes |  |  |  |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
- Manufacturer / Country
- Type / Model / Catalogue No.
| - Rating | [5 empty] | V | [5 empty] | A
- Auxiliary Switch
- Type / Model / Catalogue No.
e. | Paint
| - Manufacturer / Country |  |  | Powder Plus/Thailand
| - Type |  |  | Polyester TGIC
| - Color |  |  | Munsell 7.5 BG 6/1.5
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 1AB6-6 & 3AB6-3_SCI (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6, 3AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB6-6 , 3AB6-3
a. | Manufacturer / Country |  |  | SCI Electric PCL/Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 7 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 1000 |  | V | 50 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermoplastic
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | Schneider Electric/ China
| - Type / Model / Catalogue No. |  |  | iC60N/A9F74370 (3P ),A9F74303 (3P ) , A9F74103 ( 1P )
| - Rating |  |  | 230/400 |  | V | 0.5 ,3 ( 3P ) , 3 ( 1P ) | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | iOF 1C/O ( A9A26904 )
e. | Paint
| - Manufacturer / Country |  |  | Powder Plus/Thailand
| - Type |  |  | Polyester TGIC
| - Color |  |  | Munsell 7.5 BG 6/1.5
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 1AB6-7_SCI (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB6-7
a. | Manufacturer / Country |  |  | SCI Electric PCL/Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 8 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 1000 |  | V | 50 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermoplastic
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | Schneider Electric/ China
| - Type / Model / Catalogue No. |  |  | iC60N/A9F74103
| - Rating |  |  | 230 |  | V | 3 | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | iOF 1C/O ( A9A26904 )
e. | Paint
| - Manufacturer / Country |  |  | Powder Plus/Thailand
| - Type |  |  | Polyester TGIC
| - Color |  |  | Munsell 7.5 BG 6/1.5
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 1AB6-8_SCI (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB6-8
a. | Manufacturer / Country |  |  | SCI Electric PCL/Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 6 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 1000 |  | V | 50 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermoplastic
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | Schneider Electric/ China
| - Type / Model / Catalogue No. |  |  | A9F74303
| - Rating |  |  | 400 |  | V | 3 | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | iOF 1C/O ( A9A26904 )
e. | Paint
| - Manufacturer / Country |  |  | Powder Plus/Thailand
| - Type |  |  | Polyester TGIC
| - Color |  |  | Munsell 7.5 BG 6/1.5
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## 4AB6-3_SCI (hidden)
JUNCTION BOX AND MARSHALLING CONTROL CUBICLE
FORM PD 302,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 4AB6
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 4AB6-3
a. | Manufacturer / Country |  |  | SCI Electric PCL/Thailand
b. | Type / Type of Core |  |  |  | CT | X | PT |  |  | 11 |  | MC002
c. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PTU-80
| - Rating |  |  | 1000 |  | V | 50 | [5 empty] | A
| - Material |  |  | Non-Flammable , Thermoplastic
| - Short-Circuit Type |  |  |  | Yes |  | X |  | No
| - Suitable for Cable |  |  | up to 2 x 6 | [8 empty] | mm2
d. | Miniature Circuit Breaker
| - Manufacturer / Country |  |  | Schneider Electric/ China
| - Type / Model / Catalogue No. |  |  | iC60N/A9F74370 (3P ),A9F74303 (3P ) , A9F74103 ( 1P )
| - Rating |  |  | 230/400 |  | V | 0.5 ,3 ( 3P ) , 3 ( 1P ) | [5 empty] | A
- Auxiliary Switch
|  | - Type / Model / Catalogue No. |  | iOF 1C/O ( A9A26904 )
e. | Paint
| - Manufacturer / Country |  |  | Powder Plus/Thailand
| - Type |  |  | Polyester TGIC
| - Color |  |  | Munsell 7.5 BG 6/1.5
f. | Enclosure
| - Material |  |  | X | Stainless Steel | [5 empty] | Steel
| - Steel Sheet Thickness |  |  | 2 | [8 empty] | mm
Remark

## AB7-NHVS (550kV) (hidden)
SF6 GAS INSULATED SWITCHGEAR (GIS)
FORM PD 170
Sep. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 |  |  |  | SCHEDULE NO | [5 empty] | 1AB7&1D7
BIDDER |  | IN CONSORTIUM |  |  |  |  | ITEM NO |  |  |  |  | 1AB7-1 thru 1AB7-9 and 1D7-1 thru 1D7-9
a. | GIS Manufacturer / country of origin | [5 empty] | New Northeast Electric Group High Voltage Switchgear Co., Ltd./ China
| GIB Manufacturer / country of origin | [5 empty] | New Northeast Electric Group High Voltage Switchgear Co., Ltd./ China
b. | Type | [5 empty] | ZF15-550
c. | Applied standards | [5 empty] | IEC62271-203
d. | General rating
| - Rated voltage | [5 empty] | 550 | [12 empty] | kV
| - Maximum service voltage | [5 empty] | 550 | [12 empty] | kV
| - Rated frequency | [5 empty] | 50 | [12 empty] | Hz
| - Power frequency withstand level | [5 empty] | 740 | [12 empty] | kV
| - Lightning impulse withstand level | [5 empty] | 1675 | [12 empty] | kV
| - Switching impulse withstand level | [5 empty] | 1300 | [12 empty] | kV
- Rated continuous current
| - Busbars | [5 empty] | 4000 | [12 empty] | A
| - Feeder | [5 empty] | 4000 | [12 empty] | A
- Rated short-time (1s) withstand current for
| main and earthing circuits | [5 empty] | 63 | [12 empty] | kA
- Rated peak withstand current for main and
| earthing circuits | [5 empty] | 171 | [12 empty] | kA
e. | Type of enclosure | [5 empty] | X | Single phase enclosure
Three phase enclosure
f. | Material
| - Enclosure | [5 empty] | Aluminum alloy
| - Conductor | [5 empty] | Aluminum alloy
g. | Conductor connecting piece
| - Type | [5 empty] | Multiple contactor
| - Material | [5 empty] | Copper with silver plated
h. | SF6 Gas
| - Compliance to IEC 60376 | [5 empty] | X | Yes | [5 empty] | No
| - Manufacturer | [5 empty] | Chengdu Kemeite Special Co.,Ltd/Fujian Deer Technology Co.,Ltd
| - Purity by weight | [5 empty] | 99.7 | [12 empty] | %
| - Maximum moisture content | [5 empty] | 250 | [12 empty] | ppm
Gas Compartments
SF6 pressure information |  |  | Unit | CB | Adjacent CB | Others
[6 empty] | …VT….. |  | …Others….. |  |  |  |  | …….. |  |  |  | ……..
Rated filling pressure at 20 oC |  |  | Bar | …6….. | …5….. | …5….. |  | …5….. |  |  |  |  | …….. |  |  |  | ……..
Alarm pressure at 20 oC |  |  | Bar | …5.2….. | …4.5/5.5…. | …4.5….. |  | …4.5….. |  |  |  |  | …….. |  |  |  | ……..
Minimum functional pressure at 20 oC |  |  | Bar | …5….. | …4….. | …4….. |  | …4….. |  |  |  |  | …….. |  |  |  | ……..
Design pressure of enclosures |  |  | Bar | …8….. | …7….. | …8.5….. |  | …7….. |  |  |  |  | …….. |  |  |  | ……..
Operating pressure of pressure relief device |  |  | Bar | …11.5….. | …11.5….. | …10….. |  | …11.5….. |  |  |  |  | …….. |  |  |  | ……..
| - Pressure information in table above is given in | [5 empty] | X | Relative | [5 empty] | Absolute
| - Internal fault Short-circuit current | [5 empty] | 63 | [12 empty] | kA
- Weight of SF6 gas filling
| - Complete GIS | [5 empty] | 30177 | [12 empty] | kg
| - The largest compartment | [5 empty] | 200 | [12 empty] | kg
| - SF6 gas leakage rate | [5 empty] | ≤0.5 | [12 empty] | %/year
(Certified test record shall be submitted together with tender document
during the bidding as an evidence for consideration of evaluation)
i. | Rated supply voltage of closing and opening devices | [5 empty] | 125 | [12 empty] | Vdc
and auxiliary circuits
j. | Temperature limitations for
| - Gas dew point | [5 empty] | -33.9 | [12 empty] | °C
| - Buses and connections | [5 empty] | 105 | [12 empty] | °C
| - External parts subjected to contact by personnel | [5 empty] | 70 | [12 empty] | °C
k. | Minimum bay to bay spacing (metal-to-metal) | [5 empty] | 1500 | [12 empty] | mm*
| NB * | If EGAT considers that the specified clearance from bay to bay is inadequate for breaker maintenance, the Bidder shall be responsible for an appropriate and acceptable modification of such clearance without any price increase.
l. | Constructional features
| - Mass of the heaviest transport unit | [5 empty] | 2050 | [12 empty] | kg
| - Length of longest section for transportation | [5 empty] | 8.5 | [12 empty] | m
m. | Busducts
| - Type | [5 empty] | single phase
| - Minimum clearance to earth | [5 empty] | ≥5500 or as per requirement | [12 empty] | mm
| - Span between busbar supports | [5 empty] | 8000~15000 | [12 empty] | mm
| - Inductance | [5 empty] | 0.205 | [12 empty] | H/m
| - Capacitance | [5 empty] | 54.2 | [12 empty] | pF/m
| - Resistance of enclosure at rated frequency | [5 empty] | 5.2*10-6 | [12 empty] | W/m
| - Resistance of conductor at rated frequency | [5 empty] | 6.8*10-6 | [12 empty] | W/m
| - Surge impedance | [5 empty] | 60
n. | Space Heating
| - Install heating | [5 empty] | 100/75 | [12 empty] | W
| - Number of heater | [5 empty] | 3/3
| - Rated voltage | [5 empty] | AC230 | [12 empty] | V
Circuit Breaker
a. | Type | [5 empty] | ZF15-550(L)
b. | Single pole and/or three pole operation | [5 empty] | Single pole and three pole operated
c. | Number of breaks per pole | [5 empty] | 2
d. | Alignment of Circuit Breaker | [6 empty] | Vertical |  |  |  |  | X | Horizontal
e. | Type of interrupter | [5 empty] | X | Self blast | [5 empty] | Puffer
Etc.
f. | Applied standard | [5 empty] | IEC62271-100
g. | Rated voltage | [5 empty] | 550 | [12 empty] | kV
h. | Maximum service voltage | [5 empty] | 550 | [12 empty] | kV
i. | First pole to clear factor | [5 empty] | 1.3
j. | Power frequency withstand voltage
| - Across open switching device | [5 empty] | 740+315 | [12 empty] | kV
| - Phase to earth | [5 empty] | 740 | [12 empty] | kV
k. | Lightning impulse withstand voltage
| - Across open switching device | [5 empty] | 1675+450 | [12 empty] | kV
| - Phase to earth | [5 empty] | 1675 | [12 empty] | kV
l. | Switching impulse withstand voltage
| - Between phases | [5 empty] | 1175+450 | [12 empty] | kV
| - Phase-to-earth and across open switching device | [5 empty] | 1300 | [12 empty] | kV
m. | Frequency | [5 empty] | 50 | [12 empty] | Hz
n. | Current rating
| - Rated continuous | [5 empty] | 4000 | [12 empty] | A
| - Rated short circuit current at max kV | [5 empty] | 63 | [12 empty] | kA
| - Limited overload capacity | [5 empty] | 4400 | [12 empty] | A
o. | Interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 95.8 | [12 empty] | kA
| - 1 s short time current | [5 empty] | 63 | [12 empty] | kA
- Max opening and interrupting time at rated voltage
| - Opening time | [5 empty] | 15~25 | [12 empty] | ms
| - Interrupting time | [5 empty] | ≤40 | [12 empty] | ms
| - Current at max interrupting time | [5 empty] | 63000 (as per type test report) | [12 empty] | A
| - Interrupting time of resistive current | [5 empty] | 15~25 | [12 empty] | ms
| - Mechanism stroke | [5 empty] | 205±1 | [12 empty] | mm
| - Interrupter stroke | [5 empty] | 200±2 | [12 empty] | mm
| - Opening velocity (contact part) | [5 empty] | 9.0-9.7 | [12 empty] | m/s
p. | Asymmetrical interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 95.8 | [12 empty] | kA
q. | Closing rating
| - Closing and latching current at max kV | [5 empty] | As per IEC | [12 empty] | kA
| - Making capacity-peak at max kV | [5 empty] | 171 | [12 empty] | kA
| - Closing time at rated operations | [5 empty] | 48~60 | [12 empty] | ms
| - Closing velocity (contact touch) | [5 empty] | 4.1~5.0 | [12 empty] | m/s
r. | Capacitive current
| - Rated capacitance current switching | [5 empty] | 0.5 | [12 empty] | kA
| - Corresponding to max line length of | [5 empty] | As per IEC | [12 empty] | km
| - Rated transient overvoltage factor | [5 empty] | 2
s. | Temperature rise of contacts at nominal current | [5 empty] | ＜60 | [12 empty] | °C
t. | Operating mechanism | [5 empty] | Closing | [6 empty] | Tripping
| - Manufacturer type | [5 empty] | HDB-5
| - Mechanism type (spring, hydraulic, etc) | [5 empty] | Hydraulic spring operation
| - Operating voltage range (min/max) | [5 empty] | 106.25 |  | / | 137.5 |  |  |  | 87.5 |  |  | / | 137.5 |  | Vdc
| - Current rating of coil | [5 empty] | 2.8 | [6 empty] | 2.8 | [5 empty] | A
| - Command duration | [5 empty] | 75.2 | [6 empty] | 44.8 | [5 empty] | ms
u. | Reclosing duty cycle | [5 empty] | O-0.3s-CO-3min-CO
v. | Number of operations between servicing | [5 empty] | 10000
w. | Rated reclosing time | [5 empty] | 300 | [12 empty] | ms
x. | Net weight of each breaker | [5 empty] | 5700 | [12 empty] | kg
y. | Weight of SF6 gas filling for each breaker | [5 empty] | 150/phase | [12 empty] | kg
z. | Spring charged mechanism
| - Model no | [5 empty] | N.A.
| - Motor rating | [11 empty] | W | [6 empty] | Vdc
| - Max charging time at rated voltage | [18 empty] | s
aa. | Air compressor set or hydraulic oil pump
| - Manufacturer / country of origin | [5 empty] | HongKong /China
| - Model no | [5 empty] | 5KBB.452.255.0002
| - Number per breaker | [5 empty] | 1
| - Capacity of each set | [5 empty] | 1.8 | [12 empty] | Litre
| - Operating pressure | [5 empty] | Maximum operating pressure:700 | [12 empty] | bar
| - Motor rating | [5 empty] | 1100W, 220-250VDC per 1phase CB mechanism |  |  | W |  |  | Phase | [5 empty] | V |  | Hz
| - Net weight of each set | [5 empty] | 13 | [12 empty] | kg
| - Overall height | [5 empty] | 50 | [12 empty] | mm
| - Base dimensions | [5 empty] | 148*137 | [11 empty] | mmxmm
ab. | Air storage tank or hydraulic accumulator
| - Number per breaker | [5 empty] | 3
| - Capacity of each set | [5 empty] | 2.1 | [12 empty] | Litre
| - Working pressure | [5 empty] | 531±25 bar(Spring compression distance 83.5±1mm) | [12 empty] | bar
| - Net weight of each set | [5 empty] | 8.5 | [12 empty] | kg
| - Dimensions, diameter x length | [5 empty] | length*width*height:131*120*194 | [11 empty] | mmxmm
ac. | Stored energy requirements | [5 empty] | 2CO
ad. | Max recharging time after CO operation | [5 empty] | 30 | [12 empty] | s
Disconnecting Switch
a. | Type | [5 empty] | ZF15-550-DS
b. | Number of breaks per pole | [5 empty] | 1
c. | Applied standard | [5 empty] | IEC62271-102,IEC62271-203
d. | Rated voltage | [5 empty] | 550 | [12 empty] | kV
e. | Maximum service voltage | [5 empty] | 550 | [12 empty] | kV
f. | Power frequency withstand voltage
| - Across isolating distance | [5 empty] | 740+315 | [12 empty] | kV
| - Phase-to-earth | [5 empty] | 740 | [12 empty] | kV
g. | Lightning impulse withstand voltage
| - Across isolating distance | [5 empty] | 1675+450 | [12 empty] | kV
| - Phase-to-earth | [5 empty] | 1675 | [12 empty] | kV
h. | Switching impulse withstand voltage
| - Across isolating distance | [5 empty] | 1175+450 | [12 empty] | kV
| - Between phases | [5 empty] | 1300 | [12 empty] | kV
| - Phase-to-earth | [5 empty] | 1300 | [12 empty] | kV
i. | Frequency | [5 empty] | 50 | [12 empty] | Hz
j. | Rated continuous current | [5 empty] | 4000 | [12 empty] | A
k. | Rated peak withstand current | [5 empty] | 171 | [12 empty] | kA
l. | Rated short time (1 s) withstanding current | [5 empty] | 63 | [12 empty] | kA
m. | Type of contact | [5 empty] | Tulip
n. | Material of contact | [5 empty] | Copper with silver plated
o. | Thickness of silver on contact surfaces | [5 empty] | 0.01 | [12 empty] | mm
p. | Voltage drop across contacts at rated normal current | [5 empty] | 52 | [12 empty] | mV
q. | Operating mechanism | [5 empty] | Motor& emergency manual operation
r. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
s. | Motor Drive mechanism
| - Model no | [5 empty] | HDZ-12398-1CTH2
| - Motor rating | [5 empty] | 180 | [5 empty] | W | 125 | [5 empty] | Vdc
t. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | ≤1.7 |  |  |  | / | ≤1.5 |  |  | / | ≤1.5 |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | ≤1.7 |  |  |  | / | ≤1.5 |  |  | / | ≤1.5 |  |  |  | s
High Speed Grounding Switch
a. | Type | [5 empty] | ZF15-550-FES
b. | Rated voltage | [5 empty] | 550 | [12 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 740 | [12 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 1675 | [12 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | 1300 | [12 empty] | kV
f. | Rated short circuit making current | [5 empty] | 171 | [12 empty] | kA
g. | Rated short time (1 s) withstand current | [5 empty] | 63 | [12 empty] | kA
h. | Type of contact | [5 empty] | Tulip
i. | Material of contacts | [5 empty] | Tungsten copper alloy
j. | Thickness of silver on contacts surfaces | [5 empty] | 0.01 | [12 empty] | mm
k. | Operating mechanism | [5 empty] | Motor spring& emergency manual operation
l. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
m. | Motor Drive mechanism
| - Model no | [5 empty] | HDZ-23302C
| - Motor rating | [5 empty] | 330 | [5 empty] | W | 125 | [5 empty] | Vdc
n. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | ≤0.1 |  |  |  | / | ≤0.1 |  |  | / | ≤0.1 |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | ≤0.1 |  |  |  | / | ≤0.1 |  |  | / | ≤0.1 |  |  |  | s
Maintenance Grounding Switch
a. | Type | [5 empty] | ZF15-550-ES
b. | Rated voltage | [5 empty] | 550 | [12 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 740 | [12 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 1675 | [12 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | 1300 | [12 empty] | kV
f. | Rated short time (1 s) withstand current | [5 empty] | 63 | [12 empty] | kA
g. | Type and material of contacts | [5 empty] | Tulip/Copper with silver plated
h. | Operating mechanism | [5 empty] | Motor&emergency manual operation
i. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
j. | Motor Drive mechanism
| - Model no | [5 empty] | HDZ-11896-1CTH2
| - Motor rating | [5 empty] | 180 | [5 empty] | W | 125 | [5 empty] | Vdc
k. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | ≤2 |  |  |  | / | ≤2 |  |  | / | ≤2 |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | ≤2 |  |  |  | / | ≤2 |  |  | / | ≤2 |  |  |  | s
Voltage Transformer
a. | Manufacturer/ Country | [5 empty] | Liaoning Xinming Instrument Transformer Co.,Ltd/China
b. | Type / Model / Catalog No. | [5 empty] | JDQH-500
c. | Applied standard | [5 empty] | IEC61869-3/IEC61869-1
d. | Maximum service voltage | [5 empty] | 550 | [12 empty] | kV
e. | Rated primary voltage | [5 empty] | 500/√3 | [12 empty] | kV
f. | Voltage ratio | [5 empty] | 2500/4500& 2500/4500& 2500/4500:1
g. | Secondary voltage rating
| - No 1 secondary winding | [5 empty] | 115.47/64.15V
| - No 2 secondary winding | [5 empty] | 115.47/64.15V
| - No 3 secondary winding | [5 empty] | 115.47/64.15V
h. | Burden
| - No 1 secondary winding | [5 empty] | 75VA
| - No 2 secondary winding | [5 empty] | 75VA
| - No 3 secondary winding | [5 empty] | 75VA
| - Simultaneous | [5 empty] | 75VA
i. | Accuracy class | [5 empty] | 3P
Current Transformer
a. | Manufacturer/ Country | [5 empty] | Liaoning Xinming Instrument Transformer Co.,Ltd/China
b. | Type / Model / Catalog No. | [5 empty] | LRB-500, LRBT-500
c. | Applied standard | [5 empty] | IEC61869-1/IEC61869-2
d. | Maximum service voltage | [5 empty] | 550 | [12 empty] | kV
e. | Rated Primary Current | [5 empty] | 1500-4000 | [12 empty] | A
f. | Rated Secondary Current | [5 empty] | 1 | [12 empty] | A
g. | No of core | [5 empty] | 6
h. | Current ratio | [5 empty] | 1500/2000/4000:1//1//1//1//1//1
i. | Accuracy class | [5 empty] | 5P20(100VA)/TPY(10VA)
j. | Continuous thermal current rating factor | [5 empty] | 1
Surge Arrester
a. | Manufacturer/ Country
b. | Type / Model / Catalog No.
c. | Applied standard
d. | Continuous operating voltage (Uc) | [18 empty] | kV
e. | Class
f. | Nominal discharge current | [18 empty] | kA
g. | Rated voltage of an arrester (10 s) | [18 empty] | kV
h. | Minimum thermal energy rating (Wth) | [18 empty] | kJ/kV
i. | Net weight of each arrester | [18 empty] | kg
Bushing
a. | Manufacturer/ Country | [5 empty] | Liling Huaxin Insulator Technology Co.,Ltd./China
b. | Type / Model / Catalog No. | [5 empty] | 87705
c. | Applied standard | [5 empty] | IEC60137
d. | Maximum service voltage | [5 empty] | 550 | [12 empty] | kV
e. | Type of internal insulation | [5 empty] | SF6 gas
f. | Type of external insulation | [5 empty] | Air
g. | Nominal specific creepage distance | [5 empty] | 31 | [12 empty] | mm/kV
h. | Cantilever load | [5 empty] | 5000 | [12 empty] | N
i. | Type of line termination | [5 empty] | Terminal and Terminal connector suitable for 4*1272 MCM ACSR
SF6 Service and Storage Unit
a. Type
b. Compression pressure | [19 empty] | bar
c. Suction rate | [19 empty] | m3/hr.
d. SF6 gas recovery down to | [19 empty] | mbar
e. Vacuum pump rate | [19 empty] | m3/hr.
f. Final vacuum down to | [19 empty] | mbar
SF6 gas filling cart
a. Vacuum pump rate | [6 empty] | 16 | [12 empty] | m3/hr.
b. Evacuate rate down to | [6 empty] | ＜1 | [12 empty] | mbar
c. The weighing scale
- Range | [6 empty] | 0-120 | [12 empty] | kg
- Accuracy | [6 empty] | ±20 | [12 empty] | g
d. Pressure reducer for SF6 | [6 empty] | 0-10 | [12 empty] | bar
Portable SF6 gas leak detector
a. Sensitivity | [19 empty] | ppmv
b. Accuracy | [17 empty] | % of full scale
c. Digit display | [7 empty] | Yes | [5 empty] | No
SF6 gas quality measuring device
a. | Moisture content
| - Range of DEW point | [18 empty] | oC
| - Accuracy | [18 empty] | oC
| - Pump back function | [6 empty] | Yes | [5 empty] | No
b. | SF6 content
| - Range | [17 empty] | % volume
| - Accuracy | [17 empty] | % volume
Gas decomposition tester
a. | SO2
| - Range | [18 empty] | ppmv
| - Acuuracy | [18 empty] | %

## AB7-NHVS (245kV) (hidden)
SF6 GAS INSULATED SWITCHGEAR (GIS)
FORM PD 170
Sep. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 |  |  |  | SCHEDULE NO | [5 empty] | TIEC-S-06
BIDDER |  | IN CONSORTIUM |  |  |  |  | ITEM NO |  |  |  |  | 2AB7-1thr2AB7-9 & 2D7-1thr2D7-10
a. | GIS Manufacturer / country of origin | [5 empty] | New Northeast Electric Group High Voltage Switchgear Co., Ltd./ China
| GIB Manufacturer / country of origin | [5 empty] | New Northeast Electric Group High Voltage Switchgear Co.,Ltd /China
b. | Type | [5 empty] | ZFW20-252
c. | Applied standards | [5 empty] | IEC 62271-203
d. | General rating
| - Rated voltage | [5 empty] | 245 | [11 empty] | kV
| - Maximum service voltage | [5 empty] | 252 | [11 empty] | kV
| - Rated frequency | [5 empty] | 50 | [11 empty] | Hz
| - Power frequency withstand level | [5 empty] | 460 | [11 empty] | kV
| - Lightning impulse withstand level | [5 empty] | 1050 | [11 empty] | kV
| - Switching impulse withstand level | [5 empty] | N.A. | [11 empty] | kV
- Rated continuous current
| - Busbars | [5 empty] | 4000 | [11 empty] | A
| - Feeder | [5 empty] | 4000 | [11 empty] | A
- Rated short-time (1s) withstand current for
| main and earthing circuits | [5 empty] | 50 | [11 empty] | kA
- Rated peak withstand current for main and
| earthing circuits | [5 empty] | 125 | [11 empty] | kA
e. | Type of enclosure | [5 empty] | X | Single phase enclosure
Three phase enclosure
f. | Material
| - Enclosure | [5 empty] | Alluminum alloy
| - Conductor | [5 empty] | Alluminum alloy
g. | Conductor connecting piece
| - Type | [5 empty] | Self pressure contact / Spring contact
| - Material | [5 empty] | Cu/Ag
h. | SF6 Gas
| - Compliance to IEC 60376 | [5 empty] | X | Yes | [5 empty] | No
| - Manufacturer | [5 empty] | Chengdu Kemeite Special Co., Ltd/Fujian Deer Technology Co., Ltd
| - Purity by weight | [5 empty] | 99.997 | [11 empty] | %
| - Maximum moisture content | [5 empty] | 250 | [11 empty] | ppm
Gas Compartments
SF6 pressure information |  |  | Unit | CB | Adjacent CB | Others
[6 empty] | …….. |  | …….. |  |  |  |  | …….. |  |  | ……..
Rated filling pressure at 20 oC |  |  | Bar | …6….. | …5….. | …….. |  | …….. |  |  |  |  | …….. |  |  | ……..
Alarm pressure at 20 oC |  |  | Bar | …5.5….. | …4.5….. | …….. |  | …….. |  |  |  |  | …….. |  |  | ……..
Minimum functional pressure at 20 oC |  |  | Bar | …5….. | …4….. | …….. |  | …….. |  |  |  |  | …….. |  |  | ……..
Design pressure of enclosures |  |  | Bar | …8….. | …8/6.5….. | …….. |  | …….. |  |  |  |  | …….. |  |  | ……..
Operating pressure of pressure relief device |  |  | Bar | …11.5….. | …11.5….. | …….. |  | …….. |  |  |  |  | …….. |  |  | ……..
| - Pressure information in table above is given in | [5 empty] | X | Relative | [5 empty] | Absolute
| - Internal fault Short-circuit current | [5 empty] | 50 | [11 empty] | kA
- Weight of SF6 gas filling
| - Complete GIS | [5 empty] | 6470 | [11 empty] | kg
| - The largest compartment | [5 empty] | 150 | [11 empty] | kg
| - SF6 gas leakage rate | [5 empty] | ≤0.1 | [11 empty] | %/year
(Certified test record shall be submitted together with tender document
during the bidding as an evidence for consideration of evaluation)
i. | Rated supply voltage of closing and opening devices | [5 empty] | 125 | [11 empty] | Vdc
and auxiliary circuits
j. | Temperature limitations for
| - Gas dew point | [5 empty] | -33.9 | [11 empty] | °C
| - Buses and connections | [5 empty] | 105 | [11 empty] | °C
| - External parts subjected to contact by personnel | [5 empty] | 70 | [11 empty] | °C
k. | Minimum bay to bay spacing (metal-to-metal) | [5 empty] | 1593 | [11 empty] | mm*
| NB * | If EGAT considers that the specified clearance from bay to bay is inadequate for breaker maintenance, the Bidder shall be responsible for an appropriate and acceptable modification of such clearance without any price increase.
l. | Constructional features
| - Mass of the heaviest transport unit | [5 empty] | 8000 | [11 empty] | kg
| - Length of longest section for transportation | [5 empty] | 8 | [11 empty] | m
m. | Busducts
| - Type | [5 empty] | single phase
| - Minimum clearance to earth | [5 empty] | 1600 | [11 empty] | mm
| - Span between busbar supports | [5 empty] | 3000-5000 | [11 empty] | mm
| - Inductance | [5 empty] | 0.05 | [11 empty] | H/m
| - Capacitance | [5 empty] | 59 | [11 empty] | pF/m
| - Resistance of enclosure at rated frequency | [5 empty] | 1.3x10-6 | [11 empty] | W/m
| - Resistance of conductor at rated frequency | [5 empty] | 8x10-6 | [11 empty] | W/m
| - Surge impedance | [5 empty] | 450 ohms
n. | Space Heating
| - Install heating | [5 empty] | 200/75 | [11 empty] | W
| - Number of heater | [5 empty] | 1/1
| - Rated voltage | [5 empty] | AC 230 | [11 empty] | V
Circuit Breaker
a. | Type | [5 empty] | ZFW20-252
b. | Single pole and/or three pole operation | [5 empty] | Single pole and / or three pole operated
c. | Number of breaks per pole | [5 empty] | 1
d. | Alignment of Circuit Breaker | [6 empty] | Vertical |  |  |  |  | X | Horizontal
e. | Type of interrupter | [5 empty] | X | Self blast | [5 empty] | Puffer
Etc.
f. | Applied standard | [5 empty] | IEC 62271-100
g. | Rated voltage | [5 empty] | 245 | [11 empty] | kV
h. | Maximum service voltage | [5 empty] | 252 | [11 empty] | kV
i. | First pole to clear factor | [5 empty] | 1.3
j. | Power frequency withstand voltage
| - Across open switching device | [5 empty] | 530 | [11 empty] | kV
| - Phase to earth | [5 empty] | 460 | [11 empty] | kV
k. | Lightning impulse withstand voltage
| - Across open switching device | [5 empty] | 1200 | [11 empty] | kV
| - Phase to earth | [5 empty] | 1050 | [11 empty] | kV
l. | Switching impulse withstand voltage
| - Between phases | [5 empty] | N.A. | [11 empty] | kV
| - Phase-to-earth and across open switching device | [5 empty] | N.A. | [11 empty] | kV
m. | Frequency | [5 empty] | 50 | [11 empty] | Hz
n. | Current rating
| - Rated continuous | [5 empty] | 4000 | [11 empty] | A
| - Rated short circuit current at max kV | [5 empty] | 50 | [11 empty] | kA
| - Limited overload capacity | [5 empty] | 4400 | [11 empty] | A
o. | Interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 50 | [11 empty] | kA
| - 1 s short time current | [5 empty] | 50 | [11 empty] | kA
- Max opening and interrupting time at rated voltage
| - Opening time | [5 empty] | 20-45 | [11 empty] | ms
| - Interrupting time | [5 empty] | ≤60 | [11 empty] | ms
| - Current at max interrupting time | [5 empty] | 45000 | [11 empty] | A
| - Interrupting time of resistive current | [5 empty] | 20-45 | [11 empty] | ms
| - Mechanism stroke | [5 empty] | 190-200 | [11 empty] | mm
| - Interrupter stroke | [5 empty] | 30-38 | [11 empty] | mm
| - Opening velocity (contact part) | [5 empty] | 8.5±0.5 | [11 empty] | m/s
p. | Asymmetrical interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 50 | [11 empty] | kA
q. | Closing rating
| - Closing and latching current at max kV | [5 empty] | 125 | [11 empty] | kA
| - Making capacity-peak at max kV | [5 empty] | 125 | [11 empty] | kA
| - Closing time at rated operations | [5 empty] | 80-100 | [11 empty] | ms
| - Closing velocity (contact touch) | [5 empty] | 2.8±0.5 | [11 empty] | m/s
r. | Capacitive current
| - Rated capacitance current switching | [5 empty] | 0.125 | [11 empty] | kA
| - Corresponding to max line length of | [5 empty] | As per IEC | [11 empty] | km
| - Rated transient overvoltage factor | [5 empty] | 2
s. | Temperature rise of contacts at nominal current | [5 empty] | ≤60 | [11 empty] | °C
t. | Operating mechanism | [5 empty] | Closing | [6 empty] | Tripping
| - Manufacturer type | [5 empty] | ZFW20-252-CB
| - Mechanism type (spring, hydraulic, etc) | [5 empty] | Spring | [6 empty] | Spring
| - Operating voltage range (min/max) | [5 empty] | 106.25 |  | / | 137.5 |  |  |  | 87.5 |  | / | 137.5 |  | Vdc
| - Current rating of coil | [5 empty] | 2 | [6 empty] | 3 |  |  |  |  | A
| - Command duration | [5 empty] | 75.2 | [6 empty] | 44.8 |  |  |  |  | ms
u. | Reclosing duty cycle | [5 empty] | O-0.3s-CO-180s-CO
v. | Number of operations between servicing | [5 empty] | 10000 times
w. | Rated reclosing time | [5 empty] | 300 | [11 empty] | ms
x. | Net weight of each breaker | [5 empty] | 3690 | [11 empty] | kg
y. | Weight of SF6 gas filling for each breaker | [5 empty] | 104 | [11 empty] | kg
z. | Spring charged mechanism
| - Model no | [5 empty] | ZFW20-252-CB
| - Motor rating | [5 empty] | 600 | [5 empty] | W | 125 |  |  |  |  | Vdc
| - Max charging time at rated voltage | [5 empty] | ≤15 | [11 empty] | s
aa. | Air compressor set or hydraulic oil pump
| - Manufacturer / country of origin | [5 empty] | N.A.
- Model no
- Number per breaker
| - Capacity of each set | [17 empty] | Litre
| - Operating pressure | [17 empty] | bar
| - Motor rating | [8 empty] | W |  |  | Phase |  |  |  |  | V |  | Hz
| - Net weight of each set | [17 empty] | kg
| - Overall height | [17 empty] | mm
| - Base dimensions | [16 empty] | mmxmm
ab. | Air storage tank or hydraulic accumulator
| - Number per breaker | [5 empty] | N.A.
| - Capacity of each set | [17 empty] | Litre
| - Working pressure | [17 empty] | bar
| - Net weight of each set | [17 empty] | kg
| - Dimensions, diameter x length | [16 empty] | mmxmm
ac. | Stored energy requirements | [5 empty] | oco
ad. | Max recharging time after CO operation | [5 empty] | 15 | [11 empty] | s
Disconnecting Switch
a. | Type | [5 empty] | ZFW20-252-DS
b. | Number of breaks per pole | [5 empty] | 1
c. | Applied standard | [5 empty] | IEC 62271-102
d. | Rated voltage | [5 empty] | 245 | [11 empty] | kV
e. | Maximum service voltage | [5 empty] | 252 | [11 empty] | kV
f. | Power frequency withstand voltage
| - Across isolating distance | [5 empty] | 530 | [11 empty] | kV
| - Phase-to-earth | [5 empty] | 460 | [11 empty] | kV
g. | Lightning impulse withstand voltage
| - Across isolating distance | [5 empty] | 1200 | [11 empty] | kV
| - Phase-to-earth | [5 empty] | 1050 | [11 empty] | kV
h. | Switching impulse withstand voltage
| - Across isolating distance | [5 empty] | N.A. | [11 empty] | kV
| - Between phases | [5 empty] | N.A. | [11 empty] | kV
| - Phase-to-earth | [5 empty] | N.A. | [11 empty] | kV
i. | Frequency | [5 empty] | 50 | [11 empty] | Hz
j. | Rated continuous current | [5 empty] | 4000 | [11 empty] | A
k. | Rated peak withstand current | [5 empty] | 125 | [11 empty] | kA
l. | Rated short time (1 s) withstanding current | [5 empty] | 50 | [11 empty] | kA
m. | Type of contact | [5 empty] | Spring Contact
n. | Material of contact | [5 empty] | Cu/Ag
o. | Thickness of silver on contact surfaces | [5 empty] | 0.01 | [11 empty] | mm
p. | Voltage drop across contacts at rated normal current | [5 empty] | 94.5 | [11 empty] | mV
q. | Operating mechanism | [5 empty] | Motor & emergency manual operation
r. | Operating and control voltage | [5 empty] | 125 | [11 empty] | Vdc
s. | Motor Drive mechanism
| - Model no | [5 empty] | HDZ-13610C1
| - Motor rating | [5 empty] | 350 | [5 empty] | W | 125 |  |  |  |  | Vdc
t. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | ≤1.5 |  |  |  | / |  |  |  | / |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | ≤0.8 |  |  |  | / |  |  |  | / |  |  |  | s
High Speed Grounding Switch
a. | Type | [5 empty] | ZFW20-252-FES
b. | Rated voltage | [5 empty] | 245 | [11 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 460 | [11 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 1050 | [11 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | N.A. | [11 empty] | kV
f. | Rated short circuit making current | [5 empty] | 125 | [11 empty] | kA
g. | Rated short time (1 s) withstand current | [5 empty] | 50 | [11 empty] | kA
h. | Type of contact | [5 empty] | Self pressure contact
i. | Material of contacts | [5 empty] | Tungsten copper alloy
j. | Thickness of silver on contacts surfaces | [5 empty] | 0.01 | [11 empty] | mm
k. | Operating mechanism | [5 empty] | Motor & emergency manual operation
l. | Operating and control voltage | [5 empty] | 125 | [11 empty] | Vdc
m. | Motor Drive mechanism
| - Model no | [5 empty] | HDZ-13302CTH
| - Motor rating | [5 empty] | 350 | [5 empty] | W | 125 |  |  |  |  | Vdc
n. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | ≤7.5 |  |  |  | / |  |  |  | / |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | ≤7.5 |  |  |  | / |  |  |  | / |  |  |  | s
Maintenance Grounding Switch
a. | Type | [5 empty] | ZFW20-252-ES
b. | Rated voltage | [5 empty] | 245 | [11 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 460 | [11 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 1050 | [11 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | N.A. | [11 empty] | kV
f. | Rated short time (1 s) withstand current | [5 empty] | 50 | [11 empty] | kA
g. | Type and material of contacts | [5 empty] | Spring Contact / Cu+Ag
h. | Operating mechanism | [5 empty] | Motor & emergency manual operation
i. | Operating and control voltage | [5 empty] | 125 | [11 empty] | Vdc
j. | Motor Drive mechanism
| - Model no | [5 empty] | HDZ-13610C2
| - Motor rating | [5 empty] | 350 | [5 empty] | W | 125 |  |  |  |  | Vdc
k. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | ≤1.5 |  |  |  | / |  |  |  | / |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | ≤0.8 |  |  |  | / |  |  |  | / |  |  |  | s
Voltage Transformer
a. | Manufacturer/ Country | [5 empty] | Liaoning Xinming Instrument Transformer Co.,Ltd / China
b. | Type / Model / Catalog No. | [5 empty] | JDQH-220
c. | Applied standard | [5 empty] | IEC61869-1 / IEC61869-3
d. | Maximum service voltage | [5 empty] | 252 | [11 empty] | kV
e. | Rated primary voltage | [5 empty] | 230/ √3 | [11 empty] | kV
f. | Voltage ratio | [5 empty] | 1155/2000 & 1155/2000:1
g. | Secondary voltage rating
| - No 1 secondary winding | [5 empty] | 115/66.4 V
| - No 2 secondary winding | [5 empty] | 115/66.4 V
| - No 3 secondary winding | [5 empty] | N.A.
h. | Burden
| - No 1 secondary winding | [5 empty] | 0-15 VA
| - No 2 secondary winding | [5 empty] | 0-15 VA
| - No 3 secondary winding | [5 empty] | N.A.
| - Simultaneous | [5 empty] | 30 VA
i. | Accuracy class | [5 empty] | 3P
Current Transformer
a. | Manufacturer/ Country | [5 empty] | Liaoning Xinming Instrument Transformer Co.,Ltd / China
b. | Type / Model / Catalog No. | [5 empty] | LRB-220
c. | Applied standard | [5 empty] | IEC61869-1 / IEC61869-2
d. | Maximum service voltage | [5 empty] | 252 | [11 empty] | kV
e. | Rated Primary Current | [5 empty] | 4000 | [11 empty] | A
f. | Rated Secondary Current | [5 empty] | 1 | [11 empty] | A
g. | No of core | [5 empty] | 5
h. | Current ratio | [5 empty] | 500/1000/1500/2000/2500/3000/3500/4000 :1//1//1//1//1A
i. | Accuracy class | [5 empty] | 5P20 20VA
j. | Continuous thermal current rating factor | [5 empty] | 1
Surge Arrester
a. | Manufacturer/ Country | [5 empty] | N.A.
b. | Type / Model / Catalog No.
c. | Applied standard
d. | Continuous operating voltage (Uc) | [17 empty] | kV
e. | Class
f. | Nominal discharge current | [17 empty] | kA
g. | Rated voltage of an arrester (10 s) | [17 empty] | kV
h. | Minimum thermal energy rating (Wth) | [17 empty] | kJ/kV
i. | Net weight of each arrester | [17 empty] | kg
Bushing
a. | Manufacturer/ Country | [5 empty] | Liling Huaxin Insulator Technology Co., Ltd. /China
b. | Type / Model / Catalog No. | [5 empty] | SF6 to Air
c. | Applied standard | [5 empty] | IEC 60137
d. | Maximum service voltage | [5 empty] | 252 | [11 empty] | kV
e. | Type of internal insulation | [5 empty] | SF6 gas
f. | Type of external insulation | [5 empty] | Air
g. | Nominal specific creepage distance | [5 empty] | 31 | [11 empty] | mm/kV
h. | Cantilever load | [5 empty] | 5000 | [11 empty] | N
i. | Type of line termination | [5 empty] | Terminal and Terminal connector suitable for 4x1272 MCM ACSR
SF6 Service and Storage Unit
a. Type | [6 empty] | N.A.
b. Compression pressure | [18 empty] | bar
c. Suction rate | [18 empty] | m3/hr.
d. SF6 gas recovery down to | [18 empty] | mbar
e. Vacuum pump rate | [18 empty] | m3/hr.
f. Final vacuum down to | [18 empty] | mbar
SF6 gas filling cart
a. Vacuum pump rate | [6 empty] | 16 | [11 empty] | m3/hr.
b. Evacuate rate down to | [6 empty] | ＜1 | [11 empty] | mbar
c. The weighing scale
- Range | [6 empty] | 0-120 | [11 empty] | kg
- Accuracy | [6 empty] | ±20 | [11 empty] | g
d. Pressure reducer for SF6 | [6 empty] | 0-10 | [11 empty] | bar
Portable SF6 gas leak detector
a. Sensitivity | [6 empty] | N.A. | [11 empty] | ppmv
b. Accuracy | [16 empty] | % of full scale
c. Digit display | [7 empty] | Yes | [5 empty] | No
SF6 gas quality measuring device
a. | Moisture content
| - Range of DEW point | [5 empty] | N.A. | [11 empty] | oC
| - Accuracy | [17 empty] | oC
| - Pump back function | [6 empty] | Yes | [5 empty] | No
b. | SF6 content
| - Range | [16 empty] | % volume
| - Accuracy | [16 empty] | % volume
Gas decomposition tester
a. | SO2
| - Range | [5 empty] | N.A. | [11 empty] | ppmv
| - Acuuracy | [17 empty] | %

## AB9_550kV-Siemens (hidden)
POWER CIRCUIT BREAKER
FORM PD 156
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB9, and 3AB9
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  |  | 1AB9-1, and 3AB9-1
a. | Make and country of origin
- Circuit breaker
|  | - Make |  | Siemens Energy
|  | - Country of origin |  | Germany or China
- Steel supporting structure
|  | - Make |  | AJIKAWA & SCI OR SKY TOWER OR SST
|  | - Country of origin |  | Thailand
b. | Type
| - Interrupting medium (SF6, Vacuum, etc ) |  |  | SF6
| - Tripping |  |  |  |  | Three poles
[5 empty] | X | Single pole & Three poles
c. | Number of interrupter per pole |  |  | 2
d. | Model no |  |  | 3AP2 FI-550kV (without PIR)
e. | Applied standards |  |  | IEC 62271-1 and IEC 62271-100
f. | Rated voltage |  |  | 550 | [6 empty] | kV
g. | First pole to clear factor |  |  | 1.3
h. | Power frequency withstand voltage (rms)
| - Across open switching device |  |  | 800 | [6 empty] | kV
| - Phase-to-earth |  |  | 620 | [6 empty] | kV
i. | Lightning impulse withstand voltage, Peak
| - Across open switching device |  |  | 1150 (+315) | [6 empty] | kV
| - Phase-to-earth |  |  | 1550 | [6 empty] | kV
j. | Switching Impulse Withstand, Peak
| - Between phases |  |  | 1760 | [6 empty] | kV
| - Phase-to-earth and across open switching device |  |  | 1175 | [6 empty] | kV
k. | Frequency |  |  | 50 | [6 empty] | Hz
l. | Current rating
| - Rated continuous |  |  | 5000 | [6 empty] | A
| - Rated short time withstand current (1 s) |  |  | 63 | [6 empty] | kA
| - Rated peak withstand current |  |  | 125 | [6 empty] | kA
m. | Interrupting rating
| - Rated short circuit breaking current |  |  | 63 | [6 empty] | kA
- Max opening and interrupting time at rated control voltage
|  | - Opening time |  | 21±2 | [6 empty] | ms
|  | - Interrupting time |  | Break time ≤40 | [6 empty] | ms
| - Mechanism stroke |  |  | 170 | [6 empty] | mm
| - Interrupter stroke |  |  | 170 | [6 empty] | mm
| - Opening velocity (contact part) |  |  | 6.5±1.0 | [6 empty] | m/s
n. | Closing rating
| - Making capacity-peak |  |  | 170 | [6 empty] | kA
| - Closing time at rated operations |  |  | 63+6 | [6 empty] | ms
| - Closing velocity (contact touch) |  |  | 4.0±1.0 | [6 empty] | m/s
o. | Capacitive current
- Rated capacitance current switching
|  | - Line charging breaking current |  | 500 | [6 empty] | A
|  | - Cable charging breaking current |  | 500 | [6 empty] | A
|  | - Current (Back to back) |  | 400 (Control seitching (PSD04) will beconsider | [6 empty] | A
|  | - Inrush current (Back to back) |  | 20(Control seitching (PSD04) will beconsider | [6 empty] | kA
|  | - Frequency of inrush current |  | 4250(Control seitching (PSD04) will beconsider | [6 empty] | Hz
| - Corresponding to a max line length of |  |  | As per requirement | [6 empty] | km
| - Rated transient overvoltage factor |  |  | 2.5p.u
| - Restrike free |  |  |  |  | Class C1 |  |  | X | Class C2
p. | Temperature rise of contacts at nominal current |  |  | ≤75K | [6 empty] | °C
[5 empty] | Closing |  |  |  | Tripping
q. | Mechanism type (Spring, Hydraulic, etc) |  |  |  | spring |  |  |  | spring
r. | Control voltage rating
| - Nominal voltage |  |  |  | 125 |  |  |  | 125 |  | Vdc
| - Operating voltage range (min/max) |  |  |  | 106.25/137.5 |  |  |  | 87.5/137.5 |  | Vdc
s. | Current at nominal control voltage |  |  |  | 2.5 |  |  |  | 1.7 |  | A
t. | Command duration |  |  |  | 80 |  |  |  | 80 |  | ms
u. | Reclosing duty cycle |  |  | O + 0.3 s + CO + 15 s + CO
v. | Number of operations between servicing |  |  | for minor :3000times , for major :6000times
w. | Rated reclosing time |  |  | -343 | [6 empty] | ms
x. | Heater in control cabinet
- Continuous operated heater
|  | - Rating |  |  | 230 |  | Vac |  | 90*4 |  | W
- Thermostat controlled heater
|  | - Rating |  |  | 230 |  | Vac |  | 100*4 |  | W
|  | - Temperature setting range |  |  | -30 |  | °C to |  | 70 |  | °C
y. | Spring charged mechanism
| - Model no |  |  | FA5
- Motor rating
|  | - Nominal voltage |  | 125 | [6 empty] | Vdc
|  | - Operating voltage range (Min/Max) |  | 106.25/137.5 | [6 empty] | Vdc
|  | - Power rating |  | 0.6 | [6 empty] | kW
| - Max charging time at nominal voltage |  |  | 15 | [6 empty] | s
z. | Porcelain insulator |  |  |  | Chamber |  |  |  | Support
| - Make |  |  |  | PUCI/ADD |  |  |  | PUCI/ADD
| - Country of origin |  |  |  | China |  |  |  | China
| - Applied standard |  |  |  | IEC 62155 |  |  |  | IEC 62155
| - Creepage distance |  |  |  | 17050 |  |  |  | 17050 |  | mm
| - Type (General use or Permanent gas pressure)* |  |  |  | Permanent |  |  |  | Permanent
| - Design pressure |  |  |  | 10bar |  |  |  | 4.25Mpa |  | bar
| - Design bending |  |  |  | 40kN m(1mm) |  |  |  | 2kN m (1mm) |  | kN*m
| - Thinnest of wall thickness for electrical test* |  |  |  | 25 |  |  |  | 36/40/48 |  | mm
| - Greatest thickness for temperature-cycle test* |  |  |  | 44 |  |  |  | 44.6/52/57 |  | mm
aa. | Composite insulator
| - Make |  |  |  | N/A
| - Country of origin |  |  |  | N/A
- Applied standard
| - Housing outside insulating tube |  |  |  |  | Silicone rubber
| - Creepage distance |  |  |  | N/A | [5 empty] | mm
ab. | Height of breaker from lower energizing part to base plate |  |  | 5366 | [6 empty] | mm
ac. | Net weight of breaker |  |  | appr.11910 | [6 empty] | kg
ad. | Insulating SF6 gas required per breaker |  |  | appr.85 | [6 empty] | kg
ae. | Insulating SF6 gas furnished |  |  | appr.100 | [6 empty] | kg
(115% of actual required)
af. | Rated gas pressure at 20 °C (gauge) |  |  | 6 | [6 empty] | bar
ag. | Minimum gas pressure at 20 °C (gauge) |  |  | 5 | [6 empty] | bar
ah. | Overpressure relief device
| - Equipped |  |  |  | X | Yes |  |  |  | No
| - Operating pressure |  |  | 18-19bar | [6 empty] | kg/cm2
ai. | Each breaker completely assembled and test at the factory |  |  |  | X | Yes |  |  |  | No
aj. | Time required for field installation of each breaker |  |  | 5 | [6 empty] | Days
ak. | Surge absorber capacitor
(Supplied for 33 kV and below SF6 GCB if required)
| - Manufacturer |  |  | not included in the offer
| - Country |  |  | N/A
| - Type/Model |  |  | N/A
| - Rated voltage |  |  | N/A | [6 empty] | kV
| - BIL |  |  | N/A | [6 empty] | kV
| - Capacitance |  |  | N/A | [6 empty] | mF
al. | Controlled switching device (if required)
| - Manufacturer/ Country |  |  | Siemens Energy/ Germany
| - Type/Model |  |  | PSD04
Note.
The reference mechanical characteristics with the prescribed envelope and insulator drawing shall be submitted together with the tender document during the bidding for consideration.
*Definition based on IEC 62155 Thickness for temperature-cycle test
Thickness for temperature-cycle test

## AB9_245kV-Siemens (hidden)
POWER CIRCUIT BREAKER
FORM PD 156
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 4AB9
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  |  | 4AB9-1
a. | Make and country of origin
- Circuit breaker
|  | - Make |  | siemens energy, SHVC
|  | - Country of origin |  | Germany or China
- Steel supporting structure
|  | - Make |  | AJIKAWA & SCI OR SKY TOWER OR SST
|  | - Country of origin |  | Thailand
b. | Type
| - Interrupting medium (SF6, Vacuum, etc ) |  |  | SF6
| - Tripping |  |  |  | X | Three poles
Single pole & Three poles
c. | Number of interrupter per pole |  |  | 1
d. | Model no |  |  | 3AP1FG 245kV
e. | Applied standards |  |  | IEC 62271-1 and IEC 62271-100
f. | Rated voltage |  |  | 245 | [6 empty] | kV
g. | First pole to clear factor |  |  | 1.3
h. | Power frequency withstand voltage (rms)
| - Across open switching device |  |  | 460 | [6 empty] | kV
| - Phase-to-earth |  |  | 460 | [6 empty] | kV
i. | Lightning impulse withstand voltage, Peak
| - Across open switching device |  |  | 1050 | [6 empty] | kV
| - Phase-to-earth |  |  | 1050 | [6 empty] | kV
j. | Switching Impulse Withstand, Peak
| - Between phases |  |  | N/a | [6 empty] | kV
| - Phase-to-earth and across open switching device |  |  | N/a | [6 empty] | kV
k. | Frequency |  |  | 50 | [6 empty] | Hz
l. | Current rating
| - Rated continuous |  |  | 4000 | [6 empty] | A
| - Rated short time withstand current (1 s) |  |  | 50 | [6 empty] | kA
| - Rated peak withstand current |  |  | 125 | [6 empty] | kA
m. | Interrupting rating
| - Rated short circuit breaking current |  |  | 50 | [6 empty] | kA
- Max opening and interrupting time at rated control voltage
|  | - Opening time |  | 26±3 | [6 empty] | ms
|  | - Interrupting time |  | ≤50 | [6 empty] | ms
| - Mechanism stroke |  |  | 129±5.0 | [6 empty] | mm
| - Interrupter stroke |  |  | 150.0±5.0 (Travel of moving contact ) | [6 empty] | mm
| - Opening velocity (contact part) |  |  | 5.3±1.0 | [6 empty] | m/s
n. | Closing rating
| - Making capacity-peak |  |  | 100 | [6 empty] | kA
| - Closing time at rated operations |  |  | 66±6 | [6 empty] | ms
| - Closing velocity (contact touch) |  |  | 3.3±1.0 | [6 empty] | m/s
o. | Capacitive current
- Rated capacitance current switching
|  | - Line charging breaking current |  | 50 | [6 empty] | A
|  | - Cable charging breaking current |  | 160 | [6 empty] | A
|  | - Current (Back to back) |  | 400 | [6 empty] | A
|  | - Inrush current (Back to back) |  | 20 | [6 empty] | kA
|  | - Frequency of inrush current |  | 4.25 | [6 empty] | Hz
| - Corresponding to a max line length of |  |  | 500 | [6 empty] | km
| - Rated transient overvoltage factor |  |  | no switching overvoltages
| - Restrike free |  |  |  |  | Class C1 |  |  | X | Class C2
p. | Temperature rise of contacts at nominal current |  |  | 65 | [6 empty] | °C
[5 empty] | Closing |  |  |  | Tripping
q. | Mechanism type (Spring, Hydraulic, etc) |  |  |  | spring |  |  |  | spring
r. | Control voltage rating
| - Nominal voltage |  |  |  | 125 |  |  |  | 125 |  | Vdc
| - Operating voltage range (min/max) |  |  |  | / |  |  |  | / |  | Vdc
s. | Current at nominal control voltage |  |  |  | 2.1 |  |  |  | 1.9 |  | A
t. | Command duration |  |  |  | 80 |  |  |  | 80 |  | ms
u. | Reclosing duty cycle |  |  | CO-15s-CO
v. | Number of operations between servicing |  |  | 10000
w. | Rated reclosing time |  |  | 352 | [6 empty] | ms
x. | Heater in control cabinet
- Continuous operated heater
|  | - Rating |  |  | 230 |  | Vac |  | appr.200 |  | W
- Thermostat controlled heater
|  | - Rating |  |  | 230 |  | Vac |  | appr.90 |  | W
|  | - Temperature setting range |  |  | 0 |  | °C to |  | 40 |  | °C
y. | Spring charged mechanism
| - Model no |  |  | FA2
- Motor rating
|  | - Nominal voltage |  | 125 | [6 empty] | Vdc
|  | - Operating voltage range (Min/Max) |  | 106.25-143.75 | [6 empty] | Vdc
|  | - Power rating |  | 400 | [6 empty] | kW
| - Max charging time at nominal voltage |  |  | 15 | [6 empty] | s
z. | Porcelain insulator |  |  |  | Chamber |  |  |  | Support
| - Make |  |  |  | PUCI |  |  |  | PUCI
| - Country of origin |  |  |  | China |  |  |  | China
| - Applied standard |  |  |  | IEC 62155 |  |  |  | IEC 62155
| - Creepage distance |  |  |  | 7595 |  |  |  | 7595 |  | mm
| - Type (General use or Permanent gas pressure)* |  |  |  | General |  |  |  | General
| - Design pressure |  |  |  | 30 |  |  |  | 30 |  | bar
| - Design bending |  |  |  | 18.9 |  |  |  | 18.9 |  | kN*m
| - Thinnest of wall thickness for electrical test* |  |  |  | 110 |  |  |  | 110 |  | mm
| - Greatest thickness for temperature-cycle test* |  |  |  | 178 |  |  |  | 178 |  | mm
aa. | Composite insulator
| - Make |  |  |  | N/a
| - Country of origin |  |  |  | N/a
| - Applied standard |  |  |  | N/a
| - Housing outside insulating tube |  |  |  |  | Silicone rubber
| - Creepage distance |  |  |  | N/a | [5 empty] | mm
ab. | Height of breaker from lower energizing part to base plate |  |  | 2300 | [6 empty] | mm
ac. | Net weight of breaker |  |  | 3700 | [6 empty] | kg
ad. | Insulating SF6 gas required per breaker |  |  | 60 | [6 empty] | kg
ae. | Insulating SF6 gas furnished |  |  | as an option | [6 empty] | kg
(115% of actual required)
af. | Rated gas pressure at 20 °C (gauge) |  |  | 6 | [6 empty] | bar
ag. | Minimum gas pressure at 20 °C (gauge) |  |  | 5 | [6 empty] | bar
ah. | Overpressure relief device
| - Equipped |  |  |  | X | Yes |  |  |  | No
| - Operating pressure |  |  | 10 | [6 empty] | kg/cm2
ai. | Each breaker completely assembled and test at the factory |  |  |  | X | Yes |  |  |  | No
aj. | Time required for field installation of each breaker |  |  | 3 | [6 empty] | Days
ak. | Surge absorber capacitor
(Supplied for 33 kV and below SF6 GCB if required)
| - Manufacturer |  |  | N/a
| - Country |  |  | N/a
| - Type/Model |  |  | N/a
| - Rated voltage |  |  | N/a | [6 empty] | kV
| - BIL |  |  | N/a | [6 empty] | kV
| - Capacitance |  |  | N/a | [6 empty] | mF
al. | Controlled switching device (if required)
| - Manufacturer/ Country |  |  | N/a
| - Type/Model |  |  | N/a
Note.
The reference mechanical characteristics with the prescribed envelope and insulator drawing shall be submitted together with the tender document during the bidding for consideration.
*Definition based on IEC 62155 Thickness for temperature-cycle test
Thickness for temperature-cycle test

## AB10_550kV with ES-Hapam (hidden)
AIR SWITCHES
FORM PD 202
Apr. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 1AB10
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB10-1
a. | Manufacturer and Country of Origin
- Air Switch
|  | - Manufacturer |  | HAPAM B.V.
|  | - Country of origin |  | The Netherlands
- Steel supporting structure
|  | - Manufacturer |  | AJIKAWA & SCI OR SKY TOWER OR SST
|  | - Country of origin |  | Thailand
b. | Type /Model /Cat. No. |  |  | 3-single pole/Double Side Break/Outdoor/SSBIII-AM-550
c. | Applied Standards |  |  | IEC 62271-1 and IEC 62271-102
d. | Rated Voltage |  |  | 550 | [7 empty] | kV
e. | Power Frequency Withstand, rms
| - Across isolating distance |  |  | 800 | [7 empty] | kV
| - Phase-to-earth |  |  | 620 | [7 empty] | kV
f. | Lightning Impulse Withstand, Peak
| - Across isolating distance |  |  | 1550(+315) | [7 empty] | kV
| - Phase-to-earth |  |  | 1550 | [7 empty] | kV
g. | Switching Impulse Withstand, Peak
| - Across isolating distance |  |  | 90(+450) | [7 empty] | kV
| - Between phases |  |  | 1760 | [7 empty] | kV
| - Phase-to-earth |  |  | 11755 | [7 empty] | kV
h. | Current Rating
- Main Blades
|  | - Rated normal current |  | 4000 | [7 empty] | A
|  | - Rated short time withstand current (1 s) |  | 50 | [7 empty] | kA
|  | - Rated peak withstand current |  | 125 | [7 empty] | kA
- Grounding Blades
|  | - Rated short time withstand current |  | 50 | [7 empty] | kA
|  | - Rated peak withstand current |  | 125 | [7 empty] | kA
i. | Type and Material of Live Parts
- Main Blades
|  | - Type (Tubular, Bar, etc) |  | Tube
|  | - Material |  | Aluminum
- Grounding Blades
|  | - Type (Tubular, Bar, etc) |  | Tube
|  | - Material |  | Aluminum
j. | Contact Material
- Exposed Contacts
|  | - Fixed contacts |  | Silver Plate Copper
|  | - Moving Contacts |  | Silver Plate Copper
| - Other Current Carrying Contacts |  |  | N/A
k. | Have the Main Blades a Twist Motion in |  |  |  | X | Yes |  |  |  |  | No
Both Opening and Closing Cycles
l. | Have the Ground Blades a Double Motion in |  |  |  | X | Yes |  |  |  |  | No
Both Opening and Closing Cycles
m. | Temperature Rise under Rated Voltage,
Current and Frequency of
| - Contact |  |  | Max. 50 | [7 empty] | °C
| - Current Carrying Part |  |  | Max. 50 | [7 empty] | °C
| - Other Metalic Part |  |  | Max. 50 | [7 empty] | °C
| - Insulating Part |  |  | Max. 50 | [7 empty] | °C
n. | Mounting Position |  |  | Horizontal
o. | Phase Spacing |  |  | 7.5 | [7 empty] | m
p. | Clearance, Live Parts to Base Plate |  |  | 9 | [7 empty] | m
q. | Operating Mechanism
| - Type |  |  | Motor
| - Model /Cat. No. |  |  | MT-150
| - Operating Motion (Reciprocate, |  |  | Torsion
Torsion, etc)
| - Manual Operating Force |  |  |  | +/- 7 Nm |  | kg, |  | +/- 7 Nm | kg (peak)
| - Operating Lever Length |  |  | N/A | [7 empty] | m
| - Motor Type / Rating |  |  | 0.47 | [7 empty] | kW
| - Operating Voltage Range of Motor |  |  | Min = | 106.25 |  | Vdc, Max = |  |  | 137.5 |  | Vdc
- Method of Interlocking
|  | - Self Mechanical Interlocking between |  |  | X | Yes |  |  |  |  | No
Main Blade and Its Grounding Blade
|  | - Interlocking between Grounding Switch |  |  |  | Yes |  |  |  | X | No
and Other Corresponding Switch by Key
|  | - Key |  |  |  | Kirk
Other
- Auxiliary Switches
|  | - Number of Aux. Switches |  | 8NO+8NC
|  | - Type of Contacts |  |  |  | Interchangeable
[5 empty] | X | Fixed Type
|  | - Current Rating |  | 10 | [7 empty] | A
r. | Insulator
| - Manufacturer / country of origin |  |  | Dalian Insulator T&D Group (China)/ Suzhou (China)
| - Core Structure |  |  | Porcelain
| - Insulator Technical Ref. No. |  |  | TR391 (Post Type)
| - Leakage Distance |  |  | ≥ 13,750 | [7 empty] | mm
| - Color |  |  | Chocolate Brown
| - Weight of insulator |  |  | ≈ 379 | [7 empty] | kg
s. | Net weight of Disconnection Switch |  |  | ≈ 1740 per phase | [7 empty] | kg
(Including insulator)
t. | Transformer Magnetizing Interruption Capability |  |  | 1 | [7 empty] | A
Note. In order to guarantee the right working of the disconnector, manufacturer shall provide safety pins or spring pins to lock between rotating clamp, vertical shaft and operating mechanism shaft.

## AB10_245kV with ES-Hapam (hidden)
AIR SWITCHES
FORM PD 202
Apr. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 4AB10
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 4AB10-1
a. | Manufacturer and Country of Origin
- Air Switch
|  | - Manufacturer |  | HAPAM B.V.
|  | - Country of origin |  | The Netherlands
- Steel supporting structure
|  | - Manufacturer |  | AJIKAWA & SCI OR SKY TOWER OR SST
|  | - Country of origin |  | Thailand
b. | Type /Model /Cat. No. |  |  | 3-single pole/Double Side Break/Outdoor/SSBIII-AM-245
c. | Applied Standards |  |  | IEC 62271-1 and IEC 62271-102
d. | Rated Voltage |  |  | 245 | [7 empty] | kV
e. | Power Frequency Withstand, rms
| - Across isolating distance |  |  | 460 | [7 empty] | kV
| - Phase-to-earth |  |  | 395 | [7 empty] | kV
f. | Lightning Impulse Withstand, Peak
| - Across isolating distance |  |  | 1050 | [7 empty] | kV
| - Phase-to-earth |  |  | 950 | [7 empty] | kV
g. | Switching Impulse Withstand, Peak
| - Across isolating distance |  |  | N/A | [7 empty] | kV
| - Between phases |  |  | N/A | [7 empty] | kV
| - Phase-to-earth |  |  | N/A | [7 empty] | kV
h. | Current Rating
- Main Blades
|  | - Rated normal current |  | 4000 | [7 empty] | A
|  | - Rated short time withstand current (1 s) |  | 50 | [7 empty] | kA
|  | - Rated peak withstand current |  | 125 | [7 empty] | kA
- Grounding Blades
|  | - Rated short time withstand current |  | 50 | [7 empty] | kA
|  | - Rated peak withstand current |  | 125 | [7 empty] | kA
i. | Type and Material of Live Parts
- Main Blades
|  | - Type (Tubular, Bar, etc) |  | Rectangular Tube
|  | - Material |  | Aluminum
- Grounding Blades
|  | - Type (Tubular, Bar, etc) |  | Rectangular Tube
|  | - Material |  | Aluminum
j. | Contact Material
- Exposed Contacts
|  | - Fixed contacts |  | Silver Plate Copper
|  | - Moving Contacts |  | Silver Plate Copper
| - Other Current Carrying Contacts |  |  | N/A
k. | Have the Main Blades a Twist Motion in |  |  |  |  | Yes |  |  |  | X | No
Both Opening and Closing Cycles
l. | Have the Ground Blades a Double Motion in |  |  |  |  | Yes |  |  |  | X | No
Both Opening and Closing Cycles
m. | Temperature Rise under Rated Voltage,
Current and Frequency of
| - Contact |  |  | Max. 50 | [7 empty] | °C
| - Current Carrying Part |  |  | Max. 50 | [7 empty] | °C
| - Other Metalic Part |  |  | Max. 50 | [7 empty] | °C
| - Insulating Part |  |  | Max. 50 | [7 empty] | °C
n. | Mounting Position |  |  | Horizontal
o. | Phase Spacing |  |  | 3.5 | [7 empty] | m
p. | Clearance, Live Parts to Base Plate |  |  | 6 | [7 empty] | m
q. | Operating Mechanism
| - Type |  |  | Manual
| - Model /Cat. No. |  |  | HAC
| - Operating Motion (Reciprocate, |  |  | Torsion
Torsion, etc)
| - Manual Operating Force |  |  |  | 25 |  | kg, |  | 45 | kg (peak)
| - Operating Lever Length |  |  | N/A | [7 empty] | m
| - Motor Type / Rating |  |  | N/A / N/A | [7 empty] | kW
| - Operating Voltage Range of Motor |  |  | Min = | N/A |  | Vdc, Max = |  |  | N/A |  | Vdc
- Method of Interlocking
|  | - Self Mechanical Interlocking between |  |  | X | Yes |  |  |  |  | No
Main Blade and Its Grounding Blade
|  | - Interlocking between Grounding Switch |  |  |  | Yes |  |  |  | X | No
and Other Corresponding Switch by Key
|  | - Key |  |  |  | Kirk
[6 empty] | Other |  | N/A
- Auxiliary Switches
|  | - Number of Aux. Switches |  | 8NO+8NC
|  | - Type of Contacts |  |  |  | Interchangeable
[5 empty] | X | Fixed Type
|  | - Current Rating |  | 10 | [7 empty] | A
r. | Insulator
| - Manufacturer / country of origin |  |  | Dalian Insulator T&D Group (China)/ Suzhou (China)
| - Core Structure |  |  | Porcelain
| - Insulator Technical Ref. No. |  |  | TR308 (Post Type)
| - Leakage Distance |  |  | ≥ 6,125 | [7 empty] | mm
| - Color |  |  | Chocolate Brown
| - Weight of insulator |  |  | ≈ 160 | [7 empty] | kg
s. | Net weight of Disconnection Switch |  |  | ≈ 685 per phase | [7 empty] | kg
(Including insulator)
t. | Transformer Magnetizing Interruption Capability |  |  | 1 | [7 empty] | A
Note. In order to guarantee the right working of the disconnector, manufacturer shall provide safety pins or spring pins to lock between rotating clamp, vertical shaft and operating mechanism shaft.

## AB10_245kV without ES-Hapam (hidden)
AIR SWITCHES
FORM PD 202
Apr. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  |  | 4AB10
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 4AB10-1
a. | Manufacturer and Country of Origin
- Air Switch
|  | - Manufacturer |  | HAPAM B.V.
|  | - Country of origin |  | The Netherlands
- Steel supporting structure
|  | - Manufacturer |  | AJIKAWA & SCI OR SKY TOWER OR SST
|  | - Country of origin |  | Thailand
b. | Type /Model /Cat. No. |  |  | 3-single pole/Double Side Break/Outdoor/SSBIII-245
c. | Applied Standards |  |  | IEC 62271-1 and IEC 62271-102
d. | Rated Voltage |  |  | 245 | [7 empty] | kV
e. | Power Frequency Withstand, rms
| - Across isolating distance |  |  | 460 | [7 empty] | kV
| - Phase-to-earth |  |  | 395 | [7 empty] | kV
f. | Lightning Impulse Withstand, Peak
| - Across isolating distance |  |  | 1050 | [7 empty] | kV
| - Phase-to-earth |  |  | 950 | [7 empty] | kV
g. | Switching Impulse Withstand, Peak
| - Across isolating distance |  |  | N/A | [7 empty] | kV
| - Between phases |  |  | N/A | [7 empty] | kV
| - Phase-to-earth |  |  | N/A | [7 empty] | kV
h. | Current Rating
- Main Blades
|  | - Rated normal current |  | 4000 | [7 empty] | A
|  | - Rated short time withstand current (1 s) |  | 50 | [7 empty] | kA
|  | - Rated peak withstand current |  | 125 | [7 empty] | kA
- Grounding Blades
|  | - Rated short time withstand current |  | 50 | [7 empty] | kA
|  | - Rated peak withstand current |  | 125 | [7 empty] | kA
i. | Type and Material of Live Parts
- Main Blades
|  | - Type (Tubular, Bar, etc) |  | Rectangular Tube
|  | - Material |  | Aluminum
- Grounding Blades
|  | - Type (Tubular, Bar, etc) |  | Rectangular Tube
|  | - Material |  | Aluminum
j. | Contact Material
- Exposed Contacts
|  | - Fixed contacts |  | Silver Plate Copper
|  | - Moving Contacts |  | Silver Plate Copper
| - Other Current Carrying Contacts |  |  | N/A
k. | Have the Main Blades a Twist Motion in |  |  |  |  | Yes |  |  |  | X | No
Both Opening and Closing Cycles
l. | Have the Ground Blades a Double Motion in |  |  |  |  | Yes |  |  |  | X | No
Both Opening and Closing Cycles
m. | Temperature Rise under Rated Voltage,
Current and Frequency of
| - Contact |  |  | Max. 50 | [7 empty] | °C
| - Current Carrying Part |  |  | Max. 50 | [7 empty] | °C
| - Other Metalic Part |  |  | Max. 50 | [7 empty] | °C
| - Insulating Part |  |  | Max. 50 | [7 empty] | °C
n. | Mounting Position |  |  | Horizontal
o. | Phase Spacing |  |  | 3.5 | [7 empty] | m
p. | Clearance, Live Parts to Base Plate |  |  | 6 | [7 empty] | m
q. | Operating Mechanism
| - Type |  |  | Manual
| - Model /Cat. No. |  |  | HAC
| - Operating Motion (Reciprocate, |  |  | Torsion
Torsion, etc)
| - Manual Operating Force |  |  |  | 25 |  | kg, |  | 45 | kg (peak)
| - Operating Lever Length |  |  | N/A | [7 empty] | m
| - Motor Type / Rating |  |  | N/A / N/A | [7 empty] | kW
| - Operating Voltage Range of Motor |  |  | Min = | N/A |  | Vdc, Max = |  |  | N/A |  | Vdc
- Method of Interlocking
|  | - Self Mechanical Interlocking between |  |  | X | Yes |  |  |  |  | No
Main Blade and Its Grounding Blade
|  | - Interlocking between Grounding Switch |  |  |  | Yes |  |  |  | X | No
and Other Corresponding Switch by Key
|  | - Key |  |  |  | Kirk
[6 empty] | Other |  | N/A
- Auxiliary Switches
|  | - Number of Aux. Switches |  | 8NO+8NC
|  | - Type of Contacts |  |  |  | Interchangeable
[5 empty] | X | Fixed Type
|  | - Current Rating |  | 10 | [7 empty] | A
r. | Insulator
| - Manufacturer / country of origin |  |  | Dalian Insulator T&D Group (China)/ Suzhou (China)
| - Core Structure |  |  | Porcelain
| - Insulator Technical Ref. No. |  |  | TR308 (Post Type)
| - Leakage Distance |  |  | ≥ 6,125 | [7 empty] | mm
| - Color |  |  | Chocolate Brown
| - Weight of insulator |  |  | ≈ 160 | [7 empty] | kg
s. | Net weight of Disconnection Switch |  |  | ≈ 685 per phase | [7 empty] | kg
(Including insulator)
t. | Transformer Magnetizing Interruption Capability |  |  | 1 | [7 empty] | A
Note. In order to guarantee the right working of the disconnector, manufacturer shall provide safety pins or spring pins to lock between rotating clamp, vertical shaft and operating mechanism shaft.

## AB11 - S&C (hidden)
POWER FUSE AND HOOK STICK
FORM PD 251
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB11
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB11-1, 1AB11-2, 1D11-1 and 1D11-2
a. | Make and Country of Origin |  |  | S&C ELECTRIC CO., LTD, U.S.A.
b. | Type/Model/Cat.No |  |  | SMD-40 Cat. 192323-SP-LLB
c. | Applied Standards |  |  | ANSI C37.46
d. | Rated Maximum Voltage |  |  | 29 |  |  | kV
e. | Frequency |  |  | 50 |  |  | Hz
f. | Insulator Level
Power Frequency Withstand (Dry), rms
| Terminal-to-Terminal |  |  | 77 |  |  | kV
Impulse Withstand (BIL), Peak
| Terminal-to-Terminal |  |  | 165 |  |  | kV
g. | Current Rating |  |  | 400E |  |  | A
h. | Rated Interrupting rms Symmetrical Current |  |  | 16 |  |  | kA
i. | Mounting Position |  |  | STATION-VERTICAL
j. | Insulator
| - Make/Type |  |  | SUZHOU CHINA/STATION POST (GREY)
| - Manufacturer Reference No |  |  | 347310E2 | [5 empty] | 34.5kV
| - NEMA Technical Reference No |  |  | TR210 | [5 empty] | TR210 |  | 1 | 0.45359 | kg
| - Impulse Withstand (BIL) |  |  | 200 |  |  | kV |  |  | 200 |  | 1 | 4.448 | newtons
| - Creepage Distance |  |  | 950 |  |  | mm |  |  | 939.8 |  |  | 0.004448
- Mechanical Strength
|  | - Cantilever |  | 2000(8.90) |  |  | lb(kN) |  |  | 907.19
|  | - Tension |  | 12000(53.38) |  |  | lb(kN) |  |  | 5443.11
|  | - Mounting Bolt Circle |  | 3(7.62) |  |  | in(cm) |  |  | 7.62
k. | Rated Continuous Current of Fuse Link or Refill Unit | [7 empty] | 1 | 2 | 3 | 4 | 5 | 6
| - Item No. | 1AB11-2 |  | 20 | A,Cat.No | 823020 |  | 34.5 kV | TR210 | 200 | 939.8 | 2000(8.90) | 12000(53.38) | 3(7.62)
| - Item No. | 1D11-1 |  | 20 | A,Cat.No | 823020
| - Item No. |  |  |  | A,Cat.No | [5 empty] | 37 | 8.896 | 53.376 | 3
| - Item No. |  |  |  | A,Cat.No | [5 empty] | 939.8
l. | Weight per Phase |  |  | 60 |  |  | kg
m. | Make and Country of Origin of Hook Stick |  |  | S&C/U.S.A.

## 1AB12-1_LCUS-Precise (hidden)
LOAD CENTER UNIT SUBSTATION (LCUS)
FORM PD 434
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB12
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB12-1
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Circuit Voltage |  |  | 400 / 230 | [9 empty] | V
e. | Frequency |  |  | 50 | [9 empty] | Hz
f. | Main Bus Current Rating |  |  |  | 1000 |  | A | 1.55 |  | A/mm2
g. | Main Circuit Breaker
| - Make and Country of Origin |  |  | LS / Korea
| - Type/Model/Cat.No |  |  | AN-D
- Voltage Rating
| - Rated |  |  | 690 | [9 empty] | V
| - Maximum |  |  | 1000 | [9 empty] | V
- Current Rating
| - Continuous |  |  | 400-1000 | [9 empty] | A
| - Interrupting |  |  | 65 | [9 empty] | kA
| - Thermal Setting Range |  |  | 400-1000 | [9 empty] | A
| - Magnetic Setting Range |  |  | 600-1000 | [9 empty] | A
| - Control Circuit Voltage |  |  | 125 | [9 empty] | Vdc
| - Motor Supply Voltage |  |  | 125 | [9 empty] | Vdc
h. | Branch Circuit Breaker
| - Make and Country of Origin |  |  | LS / Korea
| - Type/Model/Cat.No |  |  | ABS203C |  | ABS203C |  | ABS203C |  | ABS203C |  | ABN403C
| - Voltage Rating |  |  | 690 |  | 690 |  | 690 |  | 690 |  | 690 |  | V
| - Frame Rating |  |  | 250 |  | 250 |  | 250 |  | 250 |  | 400 |  | A
| - Trip Rating |  |  | 100 |  | 150 |  | 200 |  | 250 |  | 400 |  | A
| - Interrupting Rating |  |  | 37 / 415 |  | 37 / 415 |  | 37 / 415 |  | 37 / 415 |  | 37 / 415 |  | kA/V
| - Magnetic Trip Adjustable |  |  |  | Yes |  | Yes |  | Yes |  | Yes |  | Yes
|  |  |  | X | No | X | No | X | No | X | No | X | No
i. | Current Transformer
| - Make and Country of Origin |  |  | Precise / Thailand
| - Accuracy Class |  |  | 0.5 | [9 empty] | VA
| - Burden |  |  | 1.5 | [9 empty] | D
| - Current Ratio |  |  | 1000/5
k. | Energy Meter
| - Make and Country of Origin |  |  | ISKRA / Slovania
| - Type |  |  | MC740
l. | Indicating Meter
| - Make and Country of Origin |  |  | ISKRA / Slovania
| - Type |  |  | CQ2207
m. | Relay
| - Make and Country of Origin |  |  | TELE / Austria
| - Type |  |  | G2PM400VSY20
n. | Dimension of LCUS Board (HxWxD) |  |  | H2300 x W2400 x D(800+25(F)+20(B)) | [7 empty] | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 | [9 empty] | mm
p. | Total Weight |  |  | 1000 | [9 empty] | kg

## AB12_LCUS-SCI (hidden)
LOAD CENTER UNIT SUBSTATION (LCUS)
FORM PD 434
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB5
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB12-1
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type |  |  | 1st ( Indoor Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Circuit Voltage |  |  | 230/400 | [9 empty] | V
e. | Frequency |  |  | 50 | [9 empty] | Hz
f. | Main Bus Current Rating |  |  |  | 1256 |  | A | 2.09 |  | A/mm2
g. | Main Circuit Breaker
| - Make and Country of Origin |  |  | ABB /China
| - Type/Model/Cat.No |  |  | E1.2B 1000
- Voltage Rating
| - Rated |  |  | 415 | [9 empty] | V
| - Maximum |  |  | 690 ( Ue ) , 1000 ( Ui ) | [9 empty] | V
- Current Rating
| - Continuous |  |  | 400-1000 | [9 empty] | A
| - Interrupting |  |  | 42 | [9 empty] | kA
| - Thermal Setting Range |  |  | 400-1000 | [9 empty] | A
| - Magnetic Setting Range |  |  | 1500-15000 | [9 empty] | A
| - Control Circuit Voltage |  |  | 125 | [9 empty] | Vdc
| - Motor Supply Voltage |  |  | 125 | [9 empty] | Vdc
h. | Branch Circuit Breaker
| - Make and Country of Origin |  |  | ABB /China
| - Type/Model/Cat.No |  |  | XT3N |  | XT3N |  | XT3N |  | XT3N |  | XT5N
| - Voltage Rating |  |  | 690 |  | 690 |  | 690 |  | 690 |  | 690 |  | V
| - Frame Rating |  |  | 250 |  | 250 |  | 250 |  | 250 |  | 400 |  | A
| - Trip Rating |  |  | 100 |  | 160 |  | 200 |  | 250 |  | 400 |  | A
| - Interrupting Rating |  |  | 36/415 |  | 36/415 |  | 36/415 |  | 36/415 |  | 36/415 |  | kA/V
| - Magnetic Trip Adjustable |  |  |  | Yes |  | Yes |  | Yes |  | Yes | X | Yes
|  |  |  | X | No | X | No | X | No |  | No |  | No
i. | Current Transformer
| - Make and Country of Origin |  |  | APN/China
| - Accuracy Class |  |  | 0.5 | [9 empty] | VA
| - Burden |  |  | 15 | [9 empty] | D
| - Current Ratio |  |  | 1000/5
k. | Energy Meter
| - Make and Country of Origin |  |  | CEWE/Italy or India
| - Type |  |  | ELITE 500 ( E500C-5401 )
l. | Indicating Meter
| - Make and Country of Origin |  |  | APN/China
| - Type |  |  | AC96-240
m. | Relay
| - Make and Country of Origin |  |  | TELE/Austria
| - Type |  |  | G2PM400VSY20
n. | Dimension of LCUS Board (HxWxD) |  |  | 2300Hx2400Wx800D | [7 empty] | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.6 | [9 empty] | mm
p. | Total Weight |  |  | Approx. 1000 | [9 empty] | kg

## 2AB12-1_LRP-Precise (hidden)
LIGHTING RELAY PANEL (LRP)
FORM PD 430.2
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 2AB12-1
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Model No |  |  | Outdoor Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 193.75 (1.55A/mm2) |  |  | A
| - Cross-section Dimension of bus |  |  | 25 x 5 |  |  | mm*mm
e. | Rated Voltage |  |  | 400 |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / ABN103c
| - Trip Rating/Max Voltage |  |  | 60 / 690 |  |  | A/V
| - Frame Rating |  |  | 100 |  |  | A
| - Interrupting Rating |  |  | 18 |  |  | kA
g. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN103c
| - Trip Rating/Max Voltage |  |  | 30 / 690 |  |  | A/V
| - Frame Rating |  |  | 100 |  |  | A
| - Interrupting Rating |  |  | 18 |  |  | kA
h. | 1-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN101d
| - Trip Rating/Max Voltage |  |  | 20 / 415 |  |  | A/V
| - Frame Rating |  |  | 100 |  |  | A
| - Interrupting Rating |  |  | 10 |  |  | kA
i. | Lighting Relay
| - Make/Type |  |  | MITSUBISHI / S-T25
| - Rated Coil Current/Voltage |  |  | 0.024 / 220 |  |  | A/V
| - Contact Current/Voltage Capacity |  |  | 30 / 380 |  |  | A/V
j. | Time Switch
| - Make/Type |  |  | PANASONIC / TB38N
| - Rated Current/Voltage |  |  | 20A/240V(Contact), 0.0083/240V(Coil) |  |  | A/V
| - Continuous operation in case of power failure |  |  | 300 |  |  | Hours
| - Contact Current Capacity |  |  | 20 |  |  | A
k. | Changeover Switch
| - Make/Type |  |  | K&N / CA10
| - Rated Current/Voltage |  |  | 20 / 600 |  |  | A/V
l. | Lighting Relay Panel Dimensions |  |  | W900 x D500 x H1350 |  |  | mm*mm*mm
m. | Sheet Steel Thickness |  |  | 2.5 |  |  | mm
n. | Total Weight |  |  | 250 |  |  | kg

## 1AB12-2_LRP-Precise (hidden)
LIGHTING RELAY PANEL (LRP)
FORM PD 430.2
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-2
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Model No |  |  | Outdoor Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 193.75 (1.55A/mm2) |  |  | A
| - Cross-section Dimension of bus |  |  | 25 x 5 |  |  | mm*mm
e. | Rated Voltage |  |  | 400 |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / ABN103c
| - Trip Rating/Max Voltage |  |  | 60 / 690 |  |  | A/V
| - Frame Rating |  |  | 100 |  |  | A
| - Interrupting Rating |  |  | 18 |  |  | kA
g. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN103c
| - Trip Rating/Max Voltage |  |  | 30 / 690 |  |  | A/V
| - Frame Rating |  |  | 100 |  |  | A
| - Interrupting Rating |  |  | 18 |  |  | kA
h. | 1-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN101d
| - Trip Rating/Max Voltage |  |  | 20 / 415 |  |  | A/V
| - Frame Rating |  |  | 100 |  |  | A
| - Interrupting Rating |  |  | 10 |  |  | kA
i. | Lighting Relay
| - Make/Type |  |  | MITSUBISHI / S-T25
| - Rated Coil Current/Voltage |  |  | 0.024 / 220 |  |  | A/V
| - Contact Current/Voltage Capacity |  |  | 30 / 380 |  |  | A/V
j. | Time Switch
| - Make/Type |  |  | PANASONIC / TB38N
| - Rated Current/Voltage |  |  | 20A/240V(Contact), 0.0083/240V(Coil) |  |  | A/V
| - Continuous operation in case of power failure |  |  | 300 |  |  | Hours
| - Contact Current Capacity |  |  | 20 |  |  | A
k. | Changeover Switch
| - Make/Type |  |  | K&N / CA10
| - Rated Current/Voltage |  |  | 20 / 600 |  |  | A/V
l. | Lighting Relay Panel Dimensions |  |  | W900 x D500 x H1350 |  |  | mm*mm*mm
m. | Sheet Steel Thickness |  |  | 2.5 |  |  | mm
n. | Total Weight |  |  | 250 |  |  | kg

## AB12_LRP-SCI (hidden)
LIGHTING RELAY PANEL (LRP)
FORM PD 430.2
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12 , 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-2 , 2AB12-1
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type / Model No |  |  | 5st ( Outdoor Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 345 |  |  | A
| - Cross-section Dimension of bus |  |  | 20x5 |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/A1A125
| - Trip Rating/Max Voltage |  |  | 60/550 |  |  | A/V
| - Frame Rating |  |  | 125 |  |  | A
| - Interrupting Rating |  |  | 10 @ 415VAC |  |  | kA
g. | 3-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1A125
| - Trip Rating/Max Voltage |  |  | 30/550 |  |  | A/V
| - Frame Rating |  |  | 125 |  |  | A
| - Interrupting Rating |  |  | 10 @ 415VAC |  |  | kA
h. | 1-Pole Branch Breaker
| - Make/Type |  |  | ABB/ A1C125
| - Trip Rating/Max Voltage |  |  | 20/415 |  |  | A/V
| - Frame Rating |  |  | 125 |  |  | A
| - Interrupting Rating |  |  | 18 @ 240VAC |  |  | kA
i. | Lighting Relay
| - Make/Type |  |  | ABB /AF16-30
| - Rated Coil Current/Voltage |  |  | 0.0096 / 100-250 |  |  | A/V
| - Contact Current/Voltage Capacity |  |  | 30 / 690 |  |  | A/V
j. | Time Switch
| - Make/Type |  |  | MULLER / SC 18.10 EASY
| - Rated Current/Voltage |  |  | 0.00435 /230 |  |  | A/V
| - Continuous operation in case of power failure |  |  | 10 Years battery-reserve |  |  | Hours
| - Contact Current Capacity |  |  | 16 |  |  | A
k. | Changeover Switch
| - Make/Type |  |  | NOVA / NCS-20M2
| - Rated Current/Voltage |  |  | 20 /690 |  |  | A/V
l. | Lighting Relay Panel Dimensions |  |  | 800Wx1350Hx400D |  |  | mm*mm*mm
m. | Sheet Steel Thickness |  |  | 2.5 |  |  | mm
n. | Total Weight |  |  | Aprrox.350 |  |  | kg

## 1AB12-5_ORB1-Precise (hidden)
COMMON CUBICLE AND OUTDOOR RECEPTACLE BOX
FORM PD ORB
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-5
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Model No |  |  | Outdoor Type
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 30 x 5 |  |  |  | mm*mm
| - Ground Bus |  |  | 30 x 5 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB / Tmax XT2N
| - Trip Rating/Max Voltage |  |  | 40 - 100 / 690 |  |  |  | A/V
| - Frame Rating |  |  | 160 |  |  |  | A
| - Interrupting Rating |  |  | 36 |  |  |  | kA
g. | Earth Leakage Circuit Breaker
| - Make/Type |  |  | SCHNEIDER / Acti9 iC60H
| - Trip Rating/Max Voltage |  |  | 20 / 240 |  |  |  | A/V
| - Frame Rating |  |  | - |  |  |  | A
| - Interrupting Rating |  |  | 10 |  |  |  | kA
| - Sensitivity |  |  | 30 |  |  |  | mA
h. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PT-600
| - Rating |  |  | 600 | V/ | 550 |  | A
- Material
| - Short-Circuit Type |  |  |  | Yes | X | No
| - Suitable for Cable |  |  | up to 240 |  |  |  | mm2
i. | Power Receptacle
| - Make/Type |  |  | SFE / SFN
| - No of Phase/No of Wire |  |  | 3 Phase / 5 Wire
| - Rated Current/Voltage |  |  | 32 / 400 |  |  |  | A/V
j. | Receptacle
| - Make/Type |  |  | PANASONIC
| - Rated Current/Voltage |  |  | 16 / 250 |  |  |  | A/V
k. | Outdoor Receptacle Box Dimensions
| - CCM type 1 | [6 empty] | mm×mm×mm
| - CCM type 2 | [6 empty] | mm×mm×mm
| - ORB1 |  |  | W(600+50(L)+50(R)) x D(300+100(F)) x H680 |  |  |  | mm×mm×mm
| - ORB2 | [6 empty] | mm×mm×mm
l. | Sheet Steel Thickness
| - CCM type 1 | [6 empty] | mm
| - CCM type 2 | [6 empty] | mm
| - ORB1 |  |  | 2.5 |  |  |  | mm
| - ORB2 | [6 empty] | mm
m. | Total Weight
| - CCM type 1 | [6 empty] | kg
| - CCM type 2 | [6 empty] | kg
| - ORB1 |  |  | 85 |  |  |  | kg
| - ORB2 | [6 empty] | kg

## 1AB12-6_ORB2-Precise (hidden)
COMMON CUBICLE AND OUTDOOR RECEPTACLE BOX
FORM PD ORB
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-6
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Model No |  |  | Outdoor Type
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 30 x 5 |  |  |  | mm*mm
| - Ground Bus |  |  | 30 x 5 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB / Tmax XT4N
| - Trip Rating/Max Voltage |  |  | 100 - 250 / 690 |  |  |  | A/V
| - Frame Rating |  |  | 250 |  |  |  | A
| - Interrupting Rating |  |  | 36 |  |  |  | kA
g. | Earth Leakage Circuit Breaker
| - Make/Type |  |  | SCHNEIDER / Acti9 iC60H
| - Trip Rating/Max Voltage |  |  | 20 / 240 |  |  |  | A/V
| - Frame Rating |  |  | - |  |  |  | A
| - Interrupting Rating |  |  | 10 |  |  |  | kA
| - Sensitivity |  |  | 30 |  |  |  | mA
h. | Terminal Block
| - Manufacturer / Country |  |  | TOGI / Japan
| - Type / Model / Catalogue No. |  |  | PT-200 / PT-600
| - Rating |  |  | 600 | V/ | 200 / 550 |  | A
- Material
| - Short-Circuit Type |  |  |  | Yes | X | No
| - Suitable for Cable |  |  | up to 95 / 240 |  |  |  | mm2
i. | Power Receptacle
| - Make/Type |  |  | SFE / SFN
| - No of Phase/No of Wire |  |  | 3 Phase / 5 Wire
| - Rated Current/Voltage |  |  | 32 / 400 |  |  |  | A/V
j. | Receptacle
| - Make/Type |  |  | PANASONIC
| - Rated Current/Voltage |  |  | 16 / 250 |  |  |  | A/V
k. | Outdoor Receptacle Box Dimensions
| - CCM type 1 | [6 empty] | mm×mm×mm
| - CCM type 2 | [6 empty] | mm×mm×mm
| - ORB1 | [6 empty] | mm×mm×mm
| - ORB2 |  |  | W(800+50(L)+50(R)) x D(300+100(F)) x H1080 |  |  |  | mm×mm×mm
l. | Sheet Steel Thickness
| - CCM type 1 | [6 empty] | mm
| - CCM type 2 | [6 empty] | mm
| - ORB1 | [6 empty] | mm
| - ORB2 |  |  | 2.5 |  |  |  | mm
m. | Total Weight
| - CCM type 1 | [6 empty] | kg
| - CCM type 2 | [6 empty] | kg
| - ORB1 | [6 empty] | kg
| - ORB2 |  |  | 100 |  |  |  | kg

## 1AB12-7_CCM1-Precise (hidden)
COMMON CUBICLE AND OUTDOOR RECEPTACLE BOX
FORM PD ORB
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-7
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Model No |  |  | Outdoor Type
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 30 x 5 |  |  |  | mm*mm
| - Ground Bus |  |  | 30 x 5 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / ABN203C
| - Trip Rating/Max Voltage |  |  | 100 , 200 / 415 |  |  |  | A/V
| - Frame Rating |  |  | 250 |  |  |  | A
| - Interrupting Rating |  |  | 26 |  |  |  | kA
g. | Earth Leakage Circuit Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / |  |  |  | A/V
| - Frame Rating | [6 empty] | A
| - Interrupting Rating | [6 empty] | kA
| - Sensitivity | [6 empty] | mA
h. | Terminal Block
| - Manufacturer / Country |  |  | /
- Type / Model / Catalogue No.
| - Rating |  |  |  | V/ |  |  | A
- Material
| - Short-Circuit Type |  |  |  | Yes |  | No
| - Suitable for Cable | [6 empty] | mm2
i. | Power Receptacle
| - Make/Type |  |  | /
- No of Phase/No of Wire
| - Rated Current/Voltage |  |  | / |  |  |  | A/V
j. | Receptacle
| - Make/Type |  |  | /
| - Rated Current/Voltage |  |  | / |  |  |  | A/V
k. | Outdoor Receptacle Box Dimensions
| - CCM type 1 |  |  | W(900+50(L)+50(R)) x D(300+100(F)) x H1080 |  |  |  | mm×mm×mm
| - CCM type 2 | [6 empty] | mm×mm×mm
| - ORB1 | [6 empty] | mm×mm×mm
| - ORB2 | [6 empty] | mm×mm×mm
l. | Sheet Steel Thickness
| - CCM type 1 |  |  | 2.5 |  |  |  | mm
| - CCM type 2 | [6 empty] | mm
| - ORB1 | [6 empty] | mm
| - ORB2 | [6 empty] | mm
m. | Total Weight
| - CCM type 1 |  |  | 100 |  |  |  | kg
| - CCM type 2 | [6 empty] | kg
| - ORB1 | [6 empty] | kg
| - ORB2 | [6 empty] | kg

## AB12_ORB1-SCI (hidden)
COMMON CUBICLE AND OUTDOOR RECEPTACLE BOX
FORM PD ORB
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-5
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type / Model No |  |  | 2wm ( Outdoor Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 20x3 |  |  |  | mm*mm
| - Ground Bus |  |  | 20x3 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 230/400 |  |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/XT2N160
| - Trip Rating/Max Voltage |  |  | 40-100/690 |  |  |  | A/V
| - Frame Rating |  |  | 160 |  |  |  | A
| - Interrupting Rating |  |  | 36 @ 415VAC |  |  |  | kA
g. | Earth Leakage Circuit Breaker
| - Make/Type |  |  | EATON /PKNM
| - Trip Rating/Max Voltage |  |  | 16/230 |  |  |  | A/V
| - Frame Rating |  |  | 63 |  |  |  | A
| - Interrupting Rating |  |  | 10 @ 230VAC |  |  |  | kA
| - Sensitivity |  |  | 30 |  |  |  | mA
h. | Terminal Block
| - Manufacturer / Country |  |  | TOGI/Japan
| - Type / Model / Catalogue No. |  |  | PT-400
| - Rating |  |  | 1000 | V/ | 400 |  | A
- Material
| - Short-Circuit Type |  |  |  | Yes | X | No
| - Suitable for Cable |  |  | Up to 240 |  |  |  | mm2
i. | Power Receptacle
| - Make/Type |  |  | FAMATEL/24333
| - No of Phase/No of Wire |  |  | 3PH/5
| - Rated Current/Voltage |  |  | 32/400 |  |  |  | A/V
j. | Receptacle
| - Make/Type |  |  | NATIONAL / WNG15923-7
| - Rated Current/Voltage |  |  | 16/250 |  |  |  | A/V
k. | Outdoor Receptacle Box Dimensions
| - CCM type 1 | [6 empty] | mm×mm×mm
| - CCM type 2 | [6 empty] | mm×mm×mm
| - ORB1 |  |  | 650Wx800Hx300D |  |  |  | mm×mm×mm
| - ORB2 | [6 empty] | mm×mm×mm
l. | Sheet Steel Thickness
| - CCM type 1 | [6 empty] | mm
| - CCM type 2 | [6 empty] | mm
| - ORB1 |  |  | 3 |  |  |  | mm
| - ORB2 | [6 empty] | mm
m. | Total Weight
| - CCM type 1 | [6 empty] | kg
| - CCM type 2 | [6 empty] | kg
| - ORB1 |  |  | Approx. 75 |  |  |  | kg
| - ORB2 | [6 empty] | kg

## AB12_ORB2-SCI (hidden)
COMMON CUBICLE AND OUTDOOR RECEPTACLE BOX
FORM PD ORB
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-6
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type / Model No |  |  | 2wm ( Outdoor Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 20x5 |  |  |  | mm*mm
| - Ground Bus |  |  | 20x5 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 230/400 |  |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/XT4N250
| - Trip Rating/Max Voltage |  |  | 100-250/690 |  |  |  | A/V
| - Frame Rating |  |  | 250 |  |  |  | A
| - Interrupting Rating |  |  | 36 @ 415VAC |  |  |  | kA
g. | Earth Leakage Circuit Breaker
| - Make/Type |  |  | EATON /PKNM
| - Trip Rating/Max Voltage |  |  | 16/230 |  |  |  | A/V
| - Frame Rating |  |  | 63 |  |  |  | A
| - Interrupting Rating |  |  | 10 @ 230VAC |  |  |  | kA
| - Sensitivity |  |  | 30 |  |  |  | mA
h. | Terminal Block
| - Manufacturer / Country |  |  | TOGI/Japan
| - Type / Model / Catalogue No. |  |  | PT-400 , PT-200
| - Rating |  |  | 1000 | V/ | 400, 240 |  | A
- Material
| - Short-Circuit Type |  |  |  | Yes | X | No
| - Suitable for Cable |  |  | Up to 240 ( PT-400 ) , Up to 100 ( PT-200 ) |  |  |  | mm2
i. | Power Receptacle
| - Make/Type |  |  | FAMATEL/24333
| - No of Phase/No of Wire |  |  | 3PH/5
| - Rated Current/Voltage |  |  | 32/400 |  |  |  | A/V
j. | Receptacle
| - Make/Type |  |  | NATIONAL / WNG15923-7
| - Rated Current/Voltage |  |  | 16/250 |  |  |  | A/V
k. | Outdoor Receptacle Box Dimensions
| - CCM type 1 | [6 empty] | mm×mm×mm
| - CCM type 2 | [6 empty] | mm×mm×mm
| - ORB1 | [6 empty] | mm×mm×mm
| - ORB2 |  |  | 800Wx1100Hx300D |  |  |  | mm×mm×mm
l. | Sheet Steel Thickness
| - CCM type 1 | [6 empty] | mm
| - CCM type 2 | [6 empty] | mm
| - ORB1 | [6 empty] | mm
| - ORB2 |  |  | 3 |  |  |  | mm
m. | Total Weight
| - CCM type 1 | [6 empty] | kg
| - CCM type 2 | [6 empty] | kg
| - ORB1 | [6 empty] | kg
| - ORB2 |  |  | Approx. 85 |  |  |  | kg

## AB12_ORB (CCM Type1)-SCI (hidden)
COMMON CUBICLE AND OUTDOOR RECEPTACLE BOX
FORM PD ORB
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-7
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type / Model No |  |  | 2wm ( Outdoor Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 20x5 |  |  |  | mm*mm
| - Ground Bus |  |  | 20x5 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 230/400 |  |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/XT3N250
| - Trip Rating/Max Voltage |  |  | 100 , 200/690 |  |  |  | A/V
| - Frame Rating |  |  | 160 , 250 |  |  |  | A
| - Interrupting Rating |  |  | 18 , 36 @ 415VAC |  |  |  | kA
g. | Earth Leakage Circuit Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / |  |  |  | A/V
| - Frame Rating | [6 empty] | A
| - Interrupting Rating | [6 empty] | kA
| - Sensitivity | [6 empty] | mA
h. | Terminal Block
| - Manufacturer / Country |  |  | /
- Type / Model / Catalogue No.
| - Rating |  |  |  | V/ |  |  | A
- Material
| - Short-Circuit Type |  |  |  | Yes |  | No
| - Suitable for Cable | [6 empty] | mm2
i. | Power Receptacle
| - Make/Type |  |  | /
- No of Phase/No of Wire
| - Rated Current/Voltage |  |  | / |  |  |  | A/V
j. | Receptacle
| - Make/Type |  |  | /
| - Rated Current/Voltage |  |  | / |  |  |  | A/V
k. | Outdoor Receptacle Box Dimensions
| - CCM type 1 |  |  | 800Wx1100Hx250D |  |  |  | mm×mm×mm
| - CCM type 2 | [6 empty] | mm×mm×mm
| - ORB1 | [6 empty] | mm×mm×mm
| - ORB2 | [6 empty] | mm×mm×mm
l. | Sheet Steel Thickness
| - CCM type 1 |  |  | 3 |  |  |  | mm
| - CCM type 2 | [6 empty] | mm
| - ORB1 | [6 empty] | mm
| - ORB2 | [6 empty] | mm
m. | Total Weight
| - CCM type 1 |  |  | Approx. 75 |  |  |  | kg
| - CCM type 2 | [6 empty] | kg
| - ORB1 | [6 empty] | kg
| - ORB2 | [6 empty] | kg

## 1AB12-9_LBS-Precise (hidden)
LOAD BREAK SWITCH AND FUSE
FORM PD LBSW
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB12-9
Panel Assembly Manufacturer / Country |  |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
A. LOAD BREAK SWITCH
a. | Make and Country of Origin |  |  | ABB / Poland
b. | Type/Model/Cat. No |  |  | NAL
c. | Applied Standards |  |  | IEC
d. | Rated Voltage |  |  | 24 |  |  |  |  | kV
e. | Maximum Service Voltage |  |  | 24 |  |  |  |  | kV
f. | Basic Impulse Voltage |  |  | 125 |  |  |  |  | kV
g. | Current Rating
- Main Switch
|  | - Rated normal current |  | 630 |  |  |  |  | A
|  | - Rated short time withstand current (1 s) |  | 25 |  |  |  |  | kA
|  | - Rated peak withstand current |  | 82 |  |  |  |  | kA
- Grounding Switch
|  | - Rated short time withstand current |  | 25 |  |  |  |  | kA
|  | - Rated peak withstand current |  | 82 |  |  |  |  | kA
h. | Phase Spacing |  |  | 275 |  |  |  |  | mm
i. | Tripping Device Actuated by Striker Pin |  |  |  |  | Yes | X | No
j. | Number of Auxiliary Switch |  |  | 2 NO + 2 NC
k. | Have confined arc quenching chamber for |  |  |  | X | Yes |  | No
air blow arc quenching
B. POWER FUSE
aa. | Make and Country of Origin |  |  | -
bb. | Type/Model/Cat. No |  |  | -
cc. | Applied Standards |  |  | -
dd. | Rated Voltage |  |  | - |  |  |  |  | kV
ee. | Maximum Service Voltage |  |  | - |  |  |  |  | kV
ff. | Basic Impulse Voltage |  |  | - |  |  |  |  | kV
gg. | Fuse Element Current Rating |  |  | - |  |  |  |  | A
hh. | Max Interrupting Rating |  |  | - |  |  |  |  | kA
ii. | Power Fuse Support Current Rating |  |  | - |  |  |  |  | kA
jj. | Fuse Blow Striker Pin Actuator |  |  |  |  | Yes |  | No

## AB12_LBS-SCI (hidden)
LOAD BREAK SWITCH AND FUSE
FORM PD LBSW
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB12-9
Panel Assembly Manufacturer / Country |  |  |  | SCI Electric PCL/Thailand
A. LOAD BREAK SWITCH
a. | Make and Country of Origin |  |  | ABB/Poland
b. | Type/Model/Cat. No |  |  | NAL24
c. | Applied Standards |  |  | IEC
d. | Rated Voltage |  |  | 24 |  |  |  |  | kV
e. | Maximum Service Voltage |  |  | .- |  |  |  |  | kV
f. | Basic Impulse Voltage |  |  | 125 |  |  |  |  | kV
g. | Current Rating
- Main Switch
|  | - Rated normal current |  | 400 |  |  |  |  | A
|  | - Rated short time withstand current (1 s) |  | 31.5 |  |  |  |  | kA
|  | - Rated peak withstand current |  | 82 |  |  |  |  | kA
- Grounding Switch
|  | - Rated short time withstand current |  | 31.5 |  |  |  |  | kA
|  | - Rated peak withstand current |  | 82 |  |  |  |  | kA
h. | Phase Spacing |  |  | 235 |  |  |  |  | mm
i. | Tripping Device Actuated by Striker Pin |  |  |  |  | Yes | X | No
j. | Number of Auxiliary Switch |  |  | 4NO+4NC
k. | Have confined arc quenching chamber for |  |  |  | X | Yes |  | No
air blow arc quenching
B. POWER FUSE
aa. | Make and Country of Origin
bb. | Type/Model/Cat. No
cc. | Applied Standards
dd. | Rated Voltage | [7 empty] | kV
ee. | Maximum Service Voltage | [7 empty] | kV
ff. | Basic Impulse Voltage | [7 empty] | kV
gg. | Fuse Element Current Rating | [7 empty] | A
hh. | Max Interrupting Rating | [7 empty] | kA
ii. | Power Fuse Support Current Rating | [7 empty] | kA
jj. | Fuse Blow Striker Pin Actuator |  |  |  |  | Yes |  | No

## 1AB12-12_AC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-12
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 465 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 9.52 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400 / 230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN101d
| - Trip Rating/Max Voltage |  |  | 32 / 415 | / |  | / |  | A/V
| - Frame Rating |  |  | 100 |  |  |  |  | A
| - Interrupting Rating |  |  | 25 |  |  |  |  | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN103c, TS100N, TS160N
| - Trip Rating/Max Voltage |  |  | 30 , 75 / 690 | 80 - 100 / 690 |  | 128 - 160 / 690 |  | A/V
| - Frame Rating |  |  | 100 | 100 |  | 160 |  | A
| - Interrupting Rating |  |  | 18 | 50 |  | 50 |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / TS400N
| - Trip Rating/Max Voltage |  |  | 160 - 400 / 690 | / |  | / |  | A/V
| - Frame Rating |  |  | 400 |  |  |  |  | A
| - Interrupting Rating |  |  | 65 |  |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | Precise / LDB-35
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 10 |  |  |  |  | VA
| - Ratio |  |  | 400 / 5
n. | Distribution Board dimension (HxWxD) |  |  | H2250 X W800 x D(500+25(F)+20(B)) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 1AB12-13_AC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-13
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 465 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 9.52 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400 / 230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN103c
| - Trip Rating/Max Voltage |  |  | 30 / 690 | 100 / 690 |  | / |  | A/V
| - Frame Rating |  |  | 100 | 100 |  |  |  | A
| - Interrupting Rating |  |  | 18 | 18 |  |  |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / TS250N
| - Trip Rating/Max Voltage |  |  | 100 - 250 / 690 | / |  | / |  | A/V
| - Frame Rating |  |  | 250 |  |  |  |  | A
| - Interrupting Rating |  |  | 50 |  |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | Precise / LDB-35
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 12.5 |  |  |  |  | VA
| - Ratio |  |  | 250 / 5
n. | Distribution Board dimension (HxWxD) |  |  | H2250 X W800 x D(500+25(F)+20(B)) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 1AB12-15_DC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-15
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN102c
| - Trip Rating/Max Voltage |  |  | 30 / 500 | 50 / 500 |  | / |  | A/Vdc
| - Frame Rating |  |  | 100 | 100 |  |  |  | A
| - Interrupting Rating |  |  | 10 | 10 |  |  |  | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | /
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | W800 x D(500+25(F)+20(B)) x H2500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 1AB12-16_DC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-16
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN102c
| - Trip Rating/Max Voltage |  |  | 50 / 500 | / |  | / |  | A/Vdc
| - Frame Rating |  |  | 100 |  |  |  |  | A
| - Interrupting Rating |  |  | 10 |  |  |  |  | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | /
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | W800 x D(500+25(F)+20(B)) x H2500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 2AB12-3_AC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 2AB12-3
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 465 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 9.52 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400 / 230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN101d
| - Trip Rating/Max Voltage |  |  | 32 / 415 | / |  | / |  | A/V
| - Frame Rating |  |  | 100 |  |  |  |  | A
| - Interrupting Rating |  |  | 25 |  |  |  |  | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN103c, TS100N, TS160N
| - Trip Rating/Max Voltage |  |  | 30 , 75 / 690 | 80 - 100 / 690 |  | 128 - 160 / 690 |  | A/V
| - Frame Rating |  |  | 100 | 100 |  | 160 |  | A
| - Interrupting Rating |  |  | 18 | 50 |  | 50 |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / TS400N
| - Trip Rating/Max Voltage |  |  | 160 - 400 / 690 | / |  | / |  | A/V
| - Frame Rating |  |  | 400 |  |  |  |  | A
| - Interrupting Rating |  |  | 65 |  |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | Precise / LDB-35
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 10 |  |  |  |  | VA
| - Ratio |  |  | 400 / 5
n. | Distribution Board dimension (HxWxD) |  |  | H2250 X W800 x D(500+25(F)+20(B)) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 2AB12-4_AC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 2AB12-4
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 465 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 9.52 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400 / 230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN103c
| - Trip Rating/Max Voltage |  |  | 30 / 690 | 100 / 690 |  | / |  | A/V
| - Frame Rating |  |  | 100 | 100 |  |  |  | A
| - Interrupting Rating |  |  | 18 | 18 |  |  |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / TS250N
| - Trip Rating/Max Voltage |  |  | 100 - 250 / 690 | / |  | / |  | A/V
| - Frame Rating |  |  | 250 |  |  |  |  | A
| - Interrupting Rating |  |  | 50 |  |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | Precise / LDB-35
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 12.5 |  |  |  |  | VA
| - Ratio |  |  | 250 / 5
n. | Distribution Board dimension (HxWxD) |  |  | H2250 X W800 x D(500+25(F)+20(B)) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 2AB12-6_DC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 2AB12-6
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN102c
| - Trip Rating/Max Voltage |  |  | 30 / 500 | 50 / 500 |  | / |  | A/Vdc
| - Frame Rating |  |  | 100 | 100 |  |  |  | A
| - Interrupting Rating |  |  | 10 | 10 |  |  |  | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | /
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | W800 x D(500+25(F)+20(B)) x H2500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 2AB12-7_DC-Precise (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 2AB12-7
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN102c
| - Trip Rating/Max Voltage |  |  | 50 / 500 | / |  | / |  | A/Vdc
| - Frame Rating |  |  | 100 |  |  |  |  | A
| - Interrupting Rating |  |  | 10 |  |  |  |  | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | /
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | W800 x D(500+25(F)+20(B)) x H2500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## AB12_AC-SCI (1) (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12 ,2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-12 , 2AB12-3
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type /Model No |  |  | 1st ( Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 468 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75x9.52 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1C125
| - Trip Rating/Max Voltage |  |  | 30/415 | / |  | / |  | A/V
| - Frame Rating |  |  | 125 |  |  |  |  | A
| - Interrupting Rating |  |  | 18 @ 240VAC |  |  |  |  | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | ABB /A1B125 , XT1B160
| - Trip Rating/Max Voltage |  |  | 30/550 | 70 , 80/550 |  | 112-160/690 |  | A/V
| - Frame Rating |  |  | 125 | 125 |  | 160 |  | A
| - Interrupting Rating |  |  | 18 @ 415VAC | 18 @ 415VAC |  | 18 @ 415VAC |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/XT5N400
| - Trip Rating/Max Voltage |  |  | 160-400/690 | / |  | / |  | A/V
| - Frame Rating |  |  | 400 |  |  |  |  | A
| - Interrupting Rating |  |  | 36 @ 415VAC |  |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | APN/CT60
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 10 |  |  |  |  | VA
| - Ratio |  |  | 400/5A
n. | Distribution Board dimension (HxWxD) |  |  | 2250x800x500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.6 |  |  |  |  | mm
p. | Total Weight |  |  | Approx. 700 |  |  |  |  | kg

## AB12_AC-SCI (2) (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12 ,2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-13 , 2AB12-4
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type /Model No |  |  | 1st ( Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 468 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75x9.52 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1B125
| - Trip Rating/Max Voltage |  |  | 30/550 | 100/550 |  | / |  | A/V
| - Frame Rating |  |  | 125 | 125 |  |  |  | A
| - Interrupting Rating |  |  | 18 @ 415VAC | 18 @ 415VAC |  |  |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/XT4N250
| - Trip Rating/Max Voltage |  |  | 100-250/690 | / |  | / |  | A/V
| - Frame Rating |  |  | 250 |  |  |  |  | A
| - Interrupting Rating |  |  | 36 @ 415VAC |  |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | ENTES/ENT
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 10 |  |  |  |  | VA
| - Ratio |  |  | 250/5A
n. | Distribution Board dimension (HxWxD) |  |  | 2250x800x500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.6 |  |  |  |  | mm
p. | Total Weight |  |  | Approx. 700 |  |  |  |  | kg

## AB12_DC-SCI (1) (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12 ,2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-15 , 2AB12-6
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type /Model No |  |  | 1st ( Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75x6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1N125
| - Trip Rating/Max Voltage |  |  | 30 /250 | 50 /250 |  | / |  | A/Vdc
| - Frame Rating |  |  | 125 | 125 |  |  |  | A
| - Interrupting Rating |  |  | 10 @ 250VDC | 10 @ 250VDC |  |  |  | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | /
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | 2500x800x500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.6 |  |  |  |  | mm
p. | Total Weight |  |  | Approx. 700 |  |  |  |  | kg

## AB12_DC-SCI (2) (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12 ,2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-16 , 2AB12-7
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type /Model No |  |  | 1st ( Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75x6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1N125
| - Trip Rating/Max Voltage |  |  | 50 ( For 45A ) /250 | 50 /250 |  | / |  | A/Vdc
| - Frame Rating |  |  | 125 | 125 |  |  |  | A
| - Interrupting Rating |  |  | 10 @ 250VDC | 10 @ 250VDC |  |  |  | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | /
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | 2500x800x500 |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.6 |  |  |  |  | mm
p. | Total Weight |  |  | Approx. 700 |  |  |  |  | kg

## 1AB12-14_Power Panel-Precise (hidden)
125 Vdc POWER PANEL
FORM PD 430.1
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB12-14
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 775 |  |  |  | A
| - Cross-section Dimension of bus |  |  | 50.8 x 9.52 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125
f. | 2-Pole Molded Case Switch
| - Make/Type |  |  | SIEMENS / 3KD38 , 3KD46
| - Current Rating/Max Voltage |  |  | 250 / 440 | 630 / 440 | / | / | A/Vdc
| - Frame Rating |  |  | 250 , 630 |  |  |  | A
g. | 2-Pole Molded Case Breaker
| - Make/Type |  |  | MITSUBISHI / NF630-SW
| - Trip Rating/Max Voltage |  |  | 630 / 250 | / | / | / | A/Vdc
| - Frame Rating |  |  | 630 |  |  |  | A
| - Interrupting Rating |  |  | 10 |  |  |  | kA
h. | Ammeter
| - Make/Type |  |  | ISKRA / BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
I. | Voltmeter (0-150 Vdc)
| - Make/Type |  |  | ISKRA / BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
j. | Voltmeter (150-0-150 Vdc)
| - Make/Type |  |  | ISKRA / BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
k. | Volmeter Selector Switch (VS)
| - Make/Type |  |  | K&N / CA10
| - Voltage Rating |  |  | 600 |  |  |  | V
| - Current Rating |  |  | 20 |  |  |  | A
l. | Under Voltage Relay (27)
| - Make/Type |  |  | TELE / G2UM300VL20
| - Adjustable Voltage Range |  |  | 15 - 285 Vdc |  |  |  | V
| - Current Rating of Contact |  |  | 5 |  |  |  | A
m. | Ground Detector
| - Make/Type |  |  | WISCO / IR195
| - Current Rating of Contact |  |  | 3A at 125 Vdc |  |  |  | A
n. | Distribution Board Dimensions |  |  | W800 x D(500+25(F)+20(B)) X H2500 |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  | kg

## 2AB12-5_Power Panel-Precise (hidden)
125 Vdc POWER PANEL
FORM PD 430.1
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 2AB12-5
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 775 |  |  |  | A
| - Cross-section Dimension of bus |  |  | 50.8 x 9.52 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125
f. | 2-Pole Molded Case Switch
| - Make/Type |  |  | SIEMENS / 3KD38 , 3KD46
| - Current Rating/Max Voltage |  |  | 250 / 440 | 630 / 440 | / | / | A/Vdc
| - Frame Rating |  |  | 250 , 630 |  |  |  | A
g. | 2-Pole Molded Case Breaker
| - Make/Type |  |  | MITSUBISHI / NF630-SW
| - Trip Rating/Max Voltage |  |  | 630 / 250 | / | / | / | A/Vdc
| - Frame Rating |  |  | 630 |  |  |  | A
| - Interrupting Rating |  |  | 10 |  |  |  | kA
h. | Ammeter
| - Make/Type |  |  | ISKRA / BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
I. | Voltmeter (0-150 Vdc)
| - Make/Type |  |  | ISKRA / BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
j. | Voltmeter (150-0-150 Vdc)
| - Make/Type |  |  | ISKRA / BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
k. | Volmeter Selector Switch (VS)
| - Make/Type |  |  | K&N / CA10
| - Voltage Rating |  |  | 600 |  |  |  | V
| - Current Rating |  |  | 20 |  |  |  | A
l. | Under Voltage Relay (27)
| - Make/Type |  |  | TELE / G2UM300VL20
| - Adjustable Voltage Range |  |  | 15 - 285 Vdc |  |  |  | V
| - Current Rating of Contact |  |  | 5 |  |  |  | A
m. | Ground Detector
| - Make/Type |  |  | WISCO / IR195
| - Current Rating of Contact |  |  | 3A at 125 Vdc |  |  |  | A
n. | Distribution Board Dimensions |  |  | W800 x D(500+25(F)+20(B)) X H2500 |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  | kg

## AB12_Power Panel-SCI (hidden)
125 Vdc POWER PANEL
FORM PD 430.1
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB12 , 2AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB12-14 , 2AB12-5
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type /Model No |  |  | 1st ( Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 895 |  |  |  | A
| - Cross-section Dimension of bus |  |  | 40x10 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125
f. | 2-Pole Molded Case Switch
| - Make/Type |  |  | SIEMENS/ 3KD3830 ,3KD4630
| - Current Rating/Max Voltage |  |  | 250/440 | 630/440 |  |  | A/Vdc
| - Frame Rating |  |  | 250/630 |  |  |  | A
g. | 2-Pole Molded Case Breaker
| - Make/Type |  |  | SIEMENS/3VA1563-5MH32-A00A ( INST.TRIP )
| - Trip Rating/Max Voltage |  |  | 630/250 | / | / | / | A/Vdc
| - Frame Rating |  |  | 1000 |  |  |  | A
| - Interrupting Rating |  |  | 35@250VDC |  |  |  | kA
h. | Ammeter
| - Make/Type |  |  | APN/DC96
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
I. | Voltmeter (0-150 Vdc)
| - Make/Type |  |  | APN/DC96
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
j. | Voltmeter (150-0-150 Vdc)
| - Make/Type |  |  | APN/DC96
| - Accuracy (% of full scale) |  |  | 1 |  |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  |  | degree
k. | Volmeter Selector Switch (VS)
| - Make/Type |  |  | NOVA/NCS20
| - Voltage Rating |  |  | 690 |  |  |  | V
| - Current Rating |  |  | 20 |  |  |  | A
l. | Under Voltage Relay (27)
| - Make/Type |  |  | TELE/G2UM300VL20
| - Adjustable Voltage Range |  |  | 15-285 |  |  |  | V
| - Current Rating of Contact |  |  | 5 |  |  |  | A
m. | Ground Detector
| - Make/Type |  |  | WISCO/IR195
| - Current Rating of Contact |  |  | 3 |  |  |  | A
n. | Distribution Board Dimensions |  |  | 2500x800x500 |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.6 |  |  |  | mm
p. | Total Weight |  |  | Approx.700 |  |  |  | kg

## 1AB13_SB BC for EPC (hidden)
VENTED STATIONARY BATTERY AND BATTERY CHARGER
FORM PD AB 13
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 |  | SCHEDULE NO. |  |  |  |  | 1AB13
BIDDER |  | IN CONSORTIUM |  |  |  | ITEM NO. |  |  |  | 1AB13
VENTED STATIONARY BATTERY
a. | Manufacturer / Country
| - Battery |  |  |  |  | HOPPECKE / GERMANY
| - Battery Rack |  |  |  |  | 4G ENGINEERING / THAILAND
| - Electrolyte |  |  |  |  | LEE CIER HUAD / THAILAND
(Bidder shall submit the certificate issued
by battery manufacturer to certify that the
proposed electrolyte is compatible with the battery.)
b. | Type / Model No. / No. of Cell |  |  |  |  | Vented Lead / OPzS / 58
| - Other, please specify |  |  |  |  | 14 OPzS 1750
| - The rating capacity |  |  |  |  | 1881 | [8 empty] | Ah
c. | Applied Standards |  |  |  |  | DIN40736-1
d. | Design, Construction, Accessories and Maintenance Tools |  |  |  |  | Conform to EGAT Specification
*in case of other, please specify in the box below :
BATTERY CHARGER
a. | Manufacturer / Country |  |  |  |  | 4G ENGINEERING / THAILAND
b. | Type / Model No. |  |  |  |  | THYRISTOR CONTROLLED /LFB3-130-250
| - The rated output current |  |  |  |  | 250 | [8 empty] | A
c. | Applied Standards |  |  |  |  | NEMA PE5
d. | Design and Construction |  |  |  |  | Conform to EGAT Specification
*in case of other, please specify in the box below :
Note :
- Certification of country of origin, production’s lot no. and manufacturing date of the battery certified by
Chamber of Commerce shall be submitted along with the Equipment at the time of shipment.
- The contractor shall provide the rating capacity of the battery and the charger as design calculation approved by EGAT
but not less than the proposed capacity as specified in this proposal without the change of the contract price.
VENTED STATIONARY BATTERY
(The contractor shall submit the following information of the stationary battery after the design calculation approved by EGAT)
a. | Type / Model No. / No. of Cell |  |  |  |  | Vented Lead / OPzS / 58
| - The rating capacity |  |  |  |  | 1881 | [8 empty] | Ah
b. | No. of Positive Plate per Cell |  |  |  |  | 14
c. | Type of Plate Construction
| - Positive Plate |  |  |  |  | TUBULAR PLATE
| - Negative Plate |  |  |  |  | GRID PLATE
d. | Material of Cell Container / Cell lid |  |  |  |  | SAN / ABS
e. | Electrolyte over Plate |  |  |  |  | 90 | [8 empty] | mm
f. | Battery Supply Condition | [5 empty] | X | Dry Charged / |  |  |  |  | Moist Charged
g. | Electrolyte
- Type / Litres per Cell
| -Total |  |  |  |  | SULFURIC ACID / 37.26
-Supplied at site (for Moist Charged)
| - Specific Gravity at 25° C |  |  |  |  | 1.24 kg / lite
| - Type of Container / Litre |  |  |  |  | PVC/ 20 lite
| - No. of Container |  |  |  |  | 119 (110% of the required electrolyte)
h. | Ampere-Hour Capacity and Discharge
Current at 25° C to 1.8 VPC
| - 10 h | [5 empty] | 1881 |  |  | Ah, | 188.1 |  |  | A
| - 1 min | [5 empty] | 13.81 |  |  | Ah, | 828.6 |  |  | A
i. | Recommended Float Charging Voltage |  |  |  |  | 2.23 | [8 empty] | V/Cell
j. | Recommended Equalize Charging Voltage | [5 empty] | 2.33 |  | V/Cell |  | 72 |  | h
and Charging Time at 0.1CA Charging Current
k. | Self Discharge per 24 h at 25° C |  |  |  |  | 1 | [8 empty] | %
l. | Expected Life |  |  |  |  | 20 | [8 empty] | year
m. | Dimension of Cell / |  | - Length |  |  | 215 | [8 empty] | mm
|  |  | - Width |  |  | 400 | [8 empty] | mm
|  |  | - Height |  |  | 815 | [8 empty] | mm
n. | Weight of Cell / |  | - Without Electrolyte |  |  | 96.1 | [8 empty] | kg
|  |  | - With Electrolyte |  |  | 142.3 | [8 empty] | kg
o. | Battery Rack
| - Rack Type |  |  |  |  | 2 |  | Rack, |  | 2 |  | Step, |  | 1 | Tier
| - Dimension / |  | - Length (Approx.) |  |  | 3500 | [8 empty] | mm
|  |  | - Width (Approx.) |  |  | 2100 | [8 empty] | mm
|  |  | - Height (Approx.) |  |  | 1170 | [8 empty] | mm
| - Weight (Approx.) |  |  |  |  | 300 | [8 empty] | kg
p. | Material of Connectors and Mounting Hardware
| - Inter Cell Connectors |  |  |  |  | Insulation connector(Flexible)
| - End Cell Connectors |  |  |  |  | Insulation connector(Flexible)
| - Bolts, Nuts and Washers |  |  |  |  | Insulated nuts with lock thread
q. | Size of End Cell Connectors (Cable Range) | [5 empty] | 35 |  | mm2 to |  |  | 120 |  | mm2
r. | Accessories
| 1. All Connector, Terminal Lugs, Bolts, | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
Nuts and Washers
| 2. Insulation Covers | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 3. Terminal Lugs for 4/0 AWG. Copper Cable | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 4. Corrosion Inhibiting Grease | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 5. Cell Numbering | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 6. Nameplate | [5 empty] | X | Yes |  |  | No |  | One(1)
s. | Maintenance Tools
| 1. Syringe Type Hydrometers | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 2. Rod Type Thermometers | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 3. Filling Syringes | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 4. Funnels | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 5. Jugs | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 6. Acid-Resistance Gloves | [5 empty] | X | Yes |  |  | No |  | Two(2) Pair
| 7. Goggles | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 8. Socket Wrench | [5 empty] | X | Yes |  |  | No |  | One(1)
| 9. Maintenance Tools Box | [5 empty] | X | Yes |  |  | No |  | One(1)
Note :
- Certification of country of origin, production’s lot no. and manufacturing date of the battery certified by
Chamber of Commerce shall be submitted along with the Equipment at the time of shipment.
- The contractor shall provide the rating capacity of the battery as design calculation approved by EGAT
but not less than the proposed capacity as specified in this proposal without the change of the contract price.
BATTERY CHARGER
(The contractor shall submit the following information of the battery charger after the design calculation approved by EGAT)
a. | Type / Model No. |  |  |  |  | Thyristor Controlled / LFB3-130-250
b. | Applied Standards |  |  |  |  | NEMA PE5
*in case of other, please specify in the box below :
*in case of other, please specify in the box below :
c. | Performance |  |  |  |  | Conform to EGAT specifiction as shown below
d. | AC Input
| - Phase |  |  |  |  | 3-phase | [9 empty] | 1 phase | 3 phase
| - Voltage Fluctuation Range |  |  |  |  | 400 ± 10% | [7 empty] | V |  | 230 ± 10% | 400 ± 10% | 400 ± 10%
| - Frequency Fluctuation Range |  |  |  |  | 50 ± 5% | [7 empty] | Hz |  | 50 ± 5% | 50 ± 5% | 50 ± 5%
| - Maximum Current |  |  |  |  | 72.2 | [7 empty] | A
e. | DC Output
| - Rated Voltage |  |  |  |  | 125 | [7 empty] | V |  | 125 | 125 | 125
| - Rated Current |  |  |  |  | 250 | [7 empty] | A
| - Float Voltage Adjustment Range |  |  |  |  | 110 |  |  | V to |  | 140 |  |  | V
| - Equalize Voltage Adjustment Range |  |  |  |  | 120 |  |  | V to |  | 150 |  |  | V
| - Output Voltage Regulation from |  |  |  |  | ± 1% | [7 empty] | % |  | ± 1% | ± 1% | ± 1%
0-100% Capacity
| - Rms Ripple Voltage without Battery |  |  |  |  | Not Exceed 2%Vrms | [7 empty] | % or mV |  | Not Exceed 2%Vrms | Not Exceed 2%Vrms | Not Exceed 2%Vrms
| - Response Time (10-90 % of Rated Output |  |  |  |  | Not Exceed 300 | [7 empty] | ms |  | Not Exceed 300 | Not Exceed 300 | Not Exceed 300
Current Step-Load Change)
| - Output Current Limit Adjustment Range |  |  |  |  | 50 |  |  | % to |  | 110 |  |  | % |  | max 110 | max 110 | 110
f. | Audible Noise Level at 1 m |  |  |  |  | Not Exceed 60 | [7 empty] | dB(A) |  | Not Exceed 60 | Not Exceed 60 | Not Exceed 60
g. | Electrical Noise Level |  |  |  |  | - | [7 empty] | dBrn-c | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
h. | Load Voltage Compensator | [17 empty] | 1 phase | 230 ± 10% | 50 ± 5% | 125 | ± 1% | Not Exceed 2%Vrms | Not Exceed 300 | 110 | Not Exceed 60
| - Input Voltage |  |  |  |  | - | [7 empty] | V |  |  |  |  | 3 phase | 400 ± 10% | 50 ± 5% | 125 | ± 1% | Not Exceed 2%Vrms | Not Exceed 300 | 110 | Not Exceed 60
| - Output Voltage |  |  |  |  | - | [7 empty] | V
| - Rated Current |  |  |  |  | - | [7 empty] | A
i. | Maximum Permissible Ambient Temperature |  |  |  |  | 40 | [7 empty] | ° C
j. | Maximum Operating Humidity |  |  |  |  | 95 | [7 empty] | %
k. | AC Protection |  |  |  |  | Breaker
l. | DC Protection |  |  |  |  | Breaker
m. | Cabinet :
| - NEMA Type |  |  |  |  | NEMA 1
| - Type Mounting |  |  |  |  | Floor
| - Width |  |  |  |  | 900 | [7 empty] | mm
| - Depth |  |  |  |  | 900 | [7 empty] | mm
| - Height |  |  |  |  | 2000 | [7 empty] | mm
| - Weight |  |  |  |  | 600 | [7 empty] | kg
| - Finish Color |  |  |  |  | ANSI 61 / RAL7036
n. | Clamp Type Pressure Connector
| - Input Cable Range |  |  |  |  | 35 |  | mm2 to |  | 120 |  | mm2
| - Output Cable Range |  |  |  |  | 70 |  | mm2 to |  | 240 |  | mm2
Accessory Equipment Furnished by Bidder : Please Check
1 | X | AC Power on Indicating Lamp
2 | X | AC Power Failure Alarm Relay & Indicating Lamp
3 | X | Ground Detection Alarm Relays with Reset Switch & Indicating Lamps
4 | X | Charger Failure Alarm Relay & Indicating Lamp
5 | X | DC Low Voltage Alarm Relay & Indicating Lamp |  |  | (Adjustable Range | 90 | to | 120 | V)
6 | X | DC High Voltage Alarm Relay & Indicating Lamp |  |  | (Adjustable Range | 120 |  | 150 | V)
7 | X | Common Remote Alarm Relay
8 | X | Float and Equalize Indicating Lamps
9 | X | 0-24 Hour Equalizing Charge Timer with Automatic Reset
*in case of other, please specify in the box below :
Note. The contractor shall provide the rating capacity of the charger as design calculation approved by EGAT, but not less than the proposed capacity as specified in this proposal without the change of the contract price.

## 2AB13_SB BC for EPC (hidden)
VENTED STATIONARY BATTERY AND BATTERY CHARGER
FORM PD AB 13
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 |  | SCHEDULE NO. |  |  |  |  | 2AB13
BIDDER |  | IN CONSORTIUM |  |  |  | ITEM NO. |  |  |  | 2AB13
VENTED STATIONARY BATTERY
a. | Manufacturer / Country
| - Battery |  |  |  |  | HOPPECKE / GERMANY
| - Battery Rack |  |  |  |  | 4G ENGINEERING / THAILAND
| - Electrolyte |  |  |  |  | LEE CIER HUAD / THAILAND
(Bidder shall submit the certificate issued
by battery manufacturer to certify that the
proposed electrolyte is compatible with the battery.)
b. | Type / Model No. / No. of Cell |  |  |  |  | Vented Lead / OPzS / 58
| - Other, please specify |  |  |  |  | 14 OPzS 1750
| - The rating capacity |  |  |  |  | 1881 | [8 empty] | Ah
c. | Applied Standards |  |  |  |  | DIN40736-1
d. | Design, Construction, Accessories and Maintenance Tools |  |  |  |  | Conform to EGAT Specification
*in case of other, please specify in the box below :
BATTERY CHARGER
a. | Manufacturer / Country |  |  |  |  | 4G ENGINEERING / THAILAND
b. | Type / Model No. |  |  |  |  | THYRISTOR CONTROLLED /LFB3-130-250
| - The rated output current |  |  |  |  | 250 | [8 empty] | A
c. | Applied Standards |  |  |  |  | NEMA PE5
d. | Design and Construction |  |  |  |  | Conform to EGAT Specification
*in case of other, please specify in the box below :
Note :
- Certification of country of origin, production’s lot no. and manufacturing date of the battery certified by
Chamber of Commerce shall be submitted along with the Equipment at the time of shipment.
- The contractor shall provide the rating capacity of the battery and the charger as design calculation approved by EGAT
but not less than the proposed capacity as specified in this proposal without the change of the contract price.
VENTED STATIONARY BATTERY
(The contractor shall submit the following information of the stationary battery after the design calculation approved by EGAT)
a. | Type / Model No. / No. of Cell |  |  |  |  | Vented Lead / 14 OPzS / 1750
| - The rating capacity |  |  |  |  | 1881 | [8 empty] | Ah
b. | No. of Positive Plate per Cell |  |  |  |  | 14
c. | Type of Plate Construction
| - Positive Plate |  |  |  |  | TUBULAR PLATE
| - Negative Plate |  |  |  |  | GRID PLATE
d. | Material of Cell Container / Cell lid |  |  |  |  | SAN / ABS
e. | Electrolyte over Plate |  |  |  |  | 90 | [8 empty] | mm
f. | Battery Supply Condition | [5 empty] | X | Dry Charged / |  |  |  |  | Moist Charged
g. | Electrolyte
- Type / Litres per Cell
| -Total |  |  |  |  | SULFURIC ACID / 37.26
-Supplied at site (for Moist Charged)
| - Specific Gravity at 25° C |  |  |  |  | 1.24 kg / lite
| - Type of Container / Litre |  |  |  |  | PVC/ 20 lite
| - No. of Container |  |  |  |  | 119 (110% of the required electrolyte)
h. | Ampere-Hour Capacity and Discharge
Current at 25° C to 1.8 VPC
| - 10 h | [5 empty] | 1881 |  |  | Ah, | 188.1 |  |  | A
| - 1 min | [5 empty] | 13.81 |  |  | Ah, | 828.6 |  |  | A
i. | Recommended Float Charging Voltage |  |  |  |  | 2.23 | [8 empty] | V/Cell
j. | Recommended Equalize Charging Voltage | [5 empty] | 2.33 |  | V/Cell |  | 72 |  | h
and Charging Time at 0.1CA Charging Current
k. | Self Discharge per 24 h at 25° C |  |  |  |  | 1 | [8 empty] | %
l. | Expected Life |  |  |  |  | 20 | [8 empty] | year
m. | Dimension of Cell / |  | - Length |  |  | 215 | [8 empty] | mm
|  |  | - Width |  |  | 400 | [8 empty] | mm
|  |  | - Height |  |  | 815 | [8 empty] | mm
n. | Weight of Cell / |  | - Without Electrolyte |  |  | 96.1 | [8 empty] | kg
|  |  | - With Electrolyte |  |  | 142.3 | [8 empty] | kg
o. | Battery Rack
| - Rack Type |  |  |  |  | 2 |  | Rack, |  | 2 |  | Step, |  | 1 | Tier
| - Dimension / |  | - Length (Approx.) |  |  | 3500 | [8 empty] | mm
|  |  | - Width (Approx.) |  |  | 2100 | [8 empty] | mm
|  |  | - Height (Approx.) |  |  | 1170 | [8 empty] | mm
| - Weight (Approx.) |  |  |  |  | 300 | [8 empty] | kg
p. | Material of Connectors and Mounting Hardware
| - Inter Cell Connectors |  |  |  |  | Insulation connector(Flexible)
| - End Cell Connectors |  |  |  |  | Insulation connector(Flexible)
| - Bolts, Nuts and Washers |  |  |  |  | Insulated nuts with lock thread
q. | Size of End Cell Connectors (Cable Range) | [5 empty] | 35 |  | mm2 to |  |  | 120 |  | mm2
r. | Accessories
| 1. All Connector, Terminal Lugs, Bolts, | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
Nuts and Washers
| 2. Insulation Covers | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 3. Terminal Lugs for 4/0 AWG. Copper Cable | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 4. Corrosion Inhibiting Grease | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 5. Cell Numbering | [5 empty] | X | Yes |  |  | No |  | One(1) Lot
| 6. Nameplate | [5 empty] | X | Yes |  |  | No |  | One(1)
s. | Maintenance Tools
| 1. Syringe Type Hydrometers | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 2. Rod Type Thermometers | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 3. Filling Syringes | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 4. Funnels | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 5. Jugs | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 6. Acid-Resistance Gloves | [5 empty] | X | Yes |  |  | No |  | Two(2) Pair
| 7. Goggles | [5 empty] | X | Yes |  |  | No |  | Two(2)
| 8. Socket Wrench | [5 empty] | X | Yes |  |  | No |  | One(1)
| 9. Maintenance Tools Box | [5 empty] | X | Yes |  |  | No |  | One(1)
Note :
- Certification of country of origin, production’s lot no. and manufacturing date of the battery certified by
Chamber of Commerce shall be submitted along with the Equipment at the time of shipment.
- The contractor shall provide the rating capacity of the battery as design calculation approved by EGAT
but not less than the proposed capacity as specified in this proposal without the change of the contract price.
BATTERY CHARGER
(The contractor shall submit the following information of the battery charger after the design calculation approved by EGAT)
a. | Type / Model No. |  |  |  |  | Thyristor Controlled / LFB3-130-250
b. | Applied Standards |  |  |  |  | NEMA PE5
*in case of other, please specify in the box below :
*in case of other, please specify in the box below :
c. | Performance |  |  |  |  | Conform to EGAT specifiction as shown below
d. | AC Input
| - Phase |  |  |  |  | 3-phase | [9 empty] | 1 phase | 3 phase
| - Voltage Fluctuation Range |  |  |  |  | 400 ± 10% | [7 empty] | V |  | 230 ± 10% | 400 ± 10% | 400 ± 10%
| - Frequency Fluctuation Range |  |  |  |  | 50 ± 5% | [7 empty] | Hz |  | 50 ± 5% | 50 ± 5% | 50 ± 5%
| - Maximum Current |  |  |  |  | 72.2 | [7 empty] | A
e. | DC Output
| - Rated Voltage |  |  |  |  | 125 | [7 empty] | V |  | 125 | 125 | 125
| - Rated Current |  |  |  |  | 250 | [7 empty] | A
| - Float Voltage Adjustment Range |  |  |  |  | 110 |  |  | V to |  | 140 |  |  | V
| - Equalize Voltage Adjustment Range |  |  |  |  | 120 |  |  | V to |  | 150 |  |  | V
| - Output Voltage Regulation from |  |  |  |  | ± 1% | [7 empty] | % |  | ± 1% | ± 1% | ± 1%
0-100% Capacity
| - Rms Ripple Voltage without Battery |  |  |  |  | Not Exceed 2%Vrms | [7 empty] | % or mV |  | Not Exceed 2%Vrms | Not Exceed 2%Vrms | Not Exceed 2%Vrms
| - Response Time (10-90 % of Rated Output |  |  |  |  | Not Exceed 300 | [7 empty] | ms |  | Not Exceed 300 | Not Exceed 300 | Not Exceed 300
Current Step-Load Change)
| - Output Current Limit Adjustment Range |  |  |  |  | 50 |  |  | % to |  | 110 |  |  | % |  | max 110 | max 110 | 110
f. | Audible Noise Level at 1 m |  |  |  |  | Not Exceed 60 | [7 empty] | dB(A) |  | Not Exceed 60 | Not Exceed 60 | Not Exceed 60
g. | Electrical Noise Level |  |  |  |  | - | [7 empty] | dBrn-c | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
h. | Load Voltage Compensator | [17 empty] | 1 phase | 230 ± 10% | 50 ± 5% | 125 | ± 1% | Not Exceed 2%Vrms | Not Exceed 300 | 110 | Not Exceed 60
| - Input Voltage |  |  |  |  | - | [7 empty] | V |  |  |  |  | 3 phase | 400 ± 10% | 50 ± 5% | 125 | ± 1% | Not Exceed 2%Vrms | Not Exceed 300 | 110 | Not Exceed 60
| - Output Voltage |  |  |  |  | - | [7 empty] | V
| - Rated Current |  |  |  |  | - | [7 empty] | A
i. | Maximum Permissible Ambient Temperature |  |  |  |  | 40 | [7 empty] | ° C
j. | Maximum Operating Humidity |  |  |  |  | 95 | [7 empty] | %
k. | AC Protection |  |  |  |  | Breaker
l. | DC Protection |  |  |  |  | Breaker
m. | Cabinet :
| - NEMA Type |  |  |  |  | NEMA 1
| - Type Mounting |  |  |  |  | Floor
| - Width |  |  |  |  | 900 | [7 empty] | mm
| - Depth |  |  |  |  | 900 | [7 empty] | mm
| - Height |  |  |  |  | 2000 | [7 empty] | mm
| - Weight |  |  |  |  | 600 | [7 empty] | kg
| - Finish Color |  |  |  |  | ANSI 61 / RAL7036
n. | Clamp Type Pressure Connector
| - Input Cable Range |  |  |  |  | 35 |  | mm2 to |  | 120 |  | mm2
| - Output Cable Range |  |  |  |  | 70 |  | mm2 to |  | 240 |  | mm2
Accessory Equipment Furnished by Bidder : Please Check
1 | X | AC Power on Indicating Lamp
2 | X | AC Power Failure Alarm Relay & Indicating Lamp
3 | X | Ground Detection Alarm Relays with Reset Switch & Indicating Lamps
4 | X | Charger Failure Alarm Relay & Indicating Lamp
5 | X | DC Low Voltage Alarm Relay & Indicating Lamp |  |  | (Adjustable Range | 90 | to | 120 | V)
6 | X | DC High Voltage Alarm Relay & Indicating Lamp |  |  | (Adjustable Range | 120 |  | 150 | V)
7 | X | Common Remote Alarm Relay
8 | X | Float and Equalize Indicating Lamps
9 | X | 0-24 Hour Equalizing Charge Timer with Automatic Reset
*in case of other, please specify in the box below :
Note. The contractor shall provide the rating capacity of the charger as design calculation approved by EGAT, but not less than the proposed capacity as specified in this proposal without the change of the contract price.

## AB14_SS - Sky Tower (hidden)
SUBSTATION STEEL STRUCTURE
FORM PD 803
Feb. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1,2,3
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. | 1AB4, 1AB10, 1AB14,2AB4,2AB5, 2AB6,2AB10,2AB14,3AB4,3AB5, 3AB6, 3AB10,3AB14
a. | Manufacturer / Country
| - Fabrication |  |  |  | SKY TOWER PUBLIC COMPANY LIMTED/THAILAND
| - Hot Dip Galvanizing |  |  |  | SKY TOWER PUBLIC COMPANY LIMTED/THAILAND
b. | Applied Standards
| - Mild Strength Structural Steel |  |  |  | JIS G3101 SS400, TIS 1227 SS400, ASTM A36, EN 10025 S275JR or Equivalent
| - High Strength Structural Steel |  |  |  | JIS G3101 SS540, TIS 1227 SS540, ASTM A572, Gr.50 & A441 or Equivalent
| - Base Plate |  |  |  | JIS G3101 SS400, TIS 1479 SS400 & SS490, ASTM A36 or Equivalent
| - Anchor Bolt |  |  |  | JIS G3101 SS400, TIS 1479 SS400 & SS490, A307 Class C or Equivalent
| - Steel Pipe |  |  |  | JIS G3444 or Equivalent
| - Step Bolt |  |  |  | JIS G3101 SS400, TIS 1227 SS400, TIS 644, ASTM A307 Class A or Equivalent
| - Connection Bolt and Nut |  |  |  | ASTM A394 Type 0 , A563 Class A or Equivalent
| - Filler |  |  |  | JIS B1256, JIS G3101 SS400, TIS 1479 SS400 or Equivalent
| - Spring Washer |  |  |  | ASA B27.1 Regular type , JIS B1251 , ASTM A394 or Equivalent
c. | Galvanizing Coating Weight |  |  |  | Conform to EGAT specification as shown below
- Structural Steel and Steel Plate
|  | Thickness 6 mm and over | [6 empty] | 702
|  | average | (more than) |  | 702 | g/m2, or | 99.3 | mm | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
|  | minimum | (more than) |  | 610 | g/m2, or | 86.3 | mm | Conform to EGAT specification as shown below | 702 | 610 | 610 | 550 | 550 | 490 | 381 | 305 | 381 | 305 | 305 | 259
|  | Thickness under 6 mm | [6 empty] | Other* (see detail in the box below) | - | - | - | - | - | - | - | - | - | - | - | -
|  | average | (more than) |  | 610 | g/m2, or | 86.3 | mm
|  | minimum | (more than) |  | 550 | g/m2, or | 77.8 | mm
- Steel Pipe
|  | average | (more than) |  | 550 | g/m2, or | 77.8 | mm | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
|  | minimum | (more than) |  | 490 | g/m2, or | 69.3 | mm | Conform to EGAT specification as shown below | 99.3 | 86.3 | 86.3 | 77.8 | 77.8 | 69.3 | 53.9 | 43.2 | 53.9 | 43.2 | 43.2 | 36.6
| - All Bolts and Nuts | [7 empty] | Other* (see detail in the box below) | - | - | - | - | - | - | - | - | - | - | - | -
|  | average | (more than) |  | 381 | g/m2, or | 53.9 | mm
|  | minimum | (more than) |  | 305 | g/m2, or | 43.2 | mm | 1: 99.3
- Washer and Filler
Thickness 5 mm and over
|  | average | (more than) |  | 381 | g/m2, or | 53.9 | mm
|  | minimum | (more than) |  | 305 | g/m2, or | 43.2 | mm
Thickness under 5 mm
|  | average | (more than) |  | 305 | g/m2, or | 43.2 | mm
|  | minimum | (more than) |  | 259 | g/m2, or | 36.6 | mm
*in case of other, please specify in the box below :
Note. In case the materials conforming to EGAT’s drawings are not available in Thailand, the contractor shall submit modification drawings and/or calculation sheet of substitute materials to EGAT for approval before fabrication.

## AB14_SS - SST (hidden)
SUBSTATION STEEL STRUCTURE
FORM PD 803
Feb. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB4, 1AB6, 1AB9, 1AB10, 1AB14, 2AB4, 2AB14, 3AB4, 3AB6, 3AB10, 4AB5 , 4AB6, 4AB9, 4AB10 and 4AB14
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. | 1AB4-2, 1AB6-4 to 1AB6-5, 1AB9-3, 1AB10-2, 1AB14-1 to 1AB10-13, 2AB4-2, 2AB14-1 to 2AB14-2, 3AB4-2, 3AB6-2, 3AB10-2, 4AB5-2, 4AB6-2, 4AB9-2, 4AB10-3 to 4AB10-4 and 4AB14-1 to 4AB14-6
a. | Manufacturer / Country
| - Fabrication |  |  |  | SIAM STEEL TOWER CO.,LTD. / THAILAND
| - Hot Dip Galvanizing |  |  |  | SIAM STEEL GALVANIZING CO.,LTD. / THAILAND
b. | Applied Standards
| - Mild Strength Structural Steel |  |  |  | JIS G3101 SS400 or ASTM A36 or Equivalent
| - High Strength Structural Steel |  |  |  | JIS G3101 SS540 or ASTM A572 Gr. 50 or Equivalent
| - Base Plate |  |  |  | JIS G3101 SS400 or ASTM A36 or Equivalent
| - Anchor Bolt |  |  |  | JIS G3101 SS400 or ASTM A36 or Equivalent
| - Steel Pipe |  |  |  | JIS G3444 STK 400 or Equivalent
| - Step Bolt |  |  |  | ASTM A307 or Equivalent
| - Connection Bolt and Nut |  |  |  | ASTM A394 Type 0 or Equivalent
| - Filler |  |  |  | JIS G3101 SS400 or Equivalent
| - Spring Washer |  |  |  | ASA B27.1 Regular Type or Equivalent
c. | Galvanizing Coating Weight |  |  |  | Conform to EGAT specification as shown below
- Structural Steel and Steel Plate
|  | Thickness 6 mm and over | [6 empty] | 702
|  | average | (more than) |  | 702 | g/m2, or | 99.3 | mm | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
|  | minimum | (more than) |  | 610 | g/m2, or | 86.3 | mm | Conform to EGAT specification as shown below | 702 | 610 | 610 | 550 | 550 | 490 | 381 | 305 | 381 | 305 | 305 | 259
|  | Thickness under 6 mm | [6 empty] | Other* (see detail in the box below) | - | - | - | - | - | - | - | - | - | - | - | -
|  | average | (more than) |  | 610 | g/m2, or | 86.3 | mm
|  | minimum | (more than) |  | 550 | g/m2, or | 77.8 | mm
- Steel Pipe
|  | average | (more than) |  | 550 | g/m2, or | 77.8 | mm | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
|  | minimum | (more than) |  | 490 | g/m2, or | 69.3 | mm | Conform to EGAT specification as shown below | 99.3 | 86.3 | 86.3 | 77.8 | 77.8 | 69.3 | 53.9 | 43.2 | 53.9 | 43.2 | 43.2 | 36.6
| - All Bolts and Nuts | [7 empty] | Other* (see detail in the box below) | - | - | - | - | - | - | - | - | - | - | - | -
|  | average | (more than) |  | 381 | g/m2, or | 53.9 | mm
|  | minimum | (more than) |  | 305 | g/m2, or | 43.2 | mm | 1: 99.3
- Washer and Filler
Thickness 5 mm and over
|  | average | (more than) |  | 381 | g/m2, or | 53.9 | mm
|  | minimum | (more than) |  | 305 | g/m2, or | 43.2 | mm
Thickness under 5 mm
|  | average | (more than) |  | 305 | g/m2, or | 43.2 | mm
|  | minimum | (more than) |  | 259 | g/m2, or | 36.6 | mm
*in case of other, please specify in the box below :
Note. In case the materials conforming to EGAT’s drawings are not available in Thailand, the contractor shall submit modification drawings and/or calculation sheet of substitute materials to EGAT for approval before fabrication.

## AB16_outdr ter 33blow - 3M (hidden)
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | 3M
|  | - Country of origin |  | USA
b. | Type / Model / Cat. NO. |  |  | Outdoor (Cold Shrink) / QT-II 5652
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Silicone Rubber
e. | Rated Voltage |  |  | Insulation Class 25 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 21.5 |  |  |  | kV
i. | Operating Environments |  |  | Heavy Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 95 | mm2 |  | Max | 185 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 21.3 | mm |  | Max | 35 | mm
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X

## AB16_cleat_Trefoil-Norma (hidden)
CABLE CLEATS
PD 326.CC
[10 empty] | Dec.2024 | [5 empty] | รายการตรวจ Cable cleat
PROPOSAL DATA | [11 empty] | comment |  |  | 1 | Material
PROCUREMENT REFERENCE |  |  | TIEC-S-06 |  | SCHEDULE NO. |  |  | 1AB16 |  |  |  | waiting for discussion with P'Ja |  |  |  | 1.1 | Metallic: | ALUMINUM 5000 SERIES
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB16-2 | [10 empty] | SS316L Stainless steel
[16 empty] | 1.2 | Composite:
[18 empty] | Metalic part | ALUMINUM 5000 SERIES
SS316L Stainless steel
a. | Manufacturer and Country of Origin | [16 empty] | non-metallic part | ANY
|  | - Manufacturer |  |  | NORMA GROUP
|  | - Country of origin |  |  | China | [9 empty] | 2 | Force/1Cleat must be more than RF EGAT
[12 empty] | ปรับให้พิจารณาแค่ type โดยขนาดของ cleat |  |  |  | 2.1 | FLAT
b. | Type/Model[1] |  |  |  | FF-T2935 | [6 empty] | จะพิจารณาในขั้นบริหารสัญญา | [5 empty] | Calculated result | #REF!
c. | For XLPE Cable Suitability[1] | [10 empty] | ตัดออกเนื่องจากพิจารณาขนาด
| - Overall Diameter Range |  |  |  | Min | 29 | mm. |  | Max | 35 | mm. | ในขั้นบริหารสัญญา
d. | Applied Standard |  |  |  | conforming with EGAT requirement (IEC 61914)
*in case of other, please specify in the box below:
e. | Classification according to material[2] |  |  |  |  | Metallic | [5 empty] | แก้รูปแบบ
Material :
[5 empty] | X | Composite
[6 empty] | Material : | Stainless Steel | [9 empty] | EGAT
[6 empty] | and | Polyolefin | [9 empty] | V | I short circuit | Lineal Spacing | FLAT Force | TREFOIL Force
f. | Resistant to electromechanical forces, withstanding more than one short circuit[3] | [15 empty] | 230 | 170 |  | #REF! | #REF!
| - Cable centre spacing (S) |  |  |  | 35 |  | mm |  |  |  |  | 0.16 | 0.17 | #REF! |  |  |  | Force
| - The peak short circuit current of the 2nd shortcircuit |  |  |  | 125 |  | kA |  |  |  |  | Trefoil wtihstrand force | [5 empty] | #REF!
| - Lineal spacing (D) |  |  |  | 600 |  | mm |  |  |  |  | Flat force withstrand force
g. | Formation |  |  |  | Trefoil | [6 empty] | ขอย้ายไปด้านบนได้ไหม
| Note [1]: | The exact size of Cable Cleat shall be confirmed after the exact overall diameter of XLPE power cable is confirmed during project stage. | [9 empty] | เพิ่มเพื่อความชัดเจน
| Note [2]: | Definitions comply with IEC 61914. metallic consisting of metal only. composite consisting of metallic and non-metallic materials.
a) Fibre reinforced resin materials are not considered to be composite.
b) Materials include any materials supplied by the manufacturer as part of a cable cleat or intermediate restraint or with a cable cleat or intermediate restraint in the same packaging. This may include fixings such as nuts, bolts, screws, washers, springs and pins.
| Note [3]: | The data specified in this item shall conform to the Type Test Report of the type proposed.
| Note [4]: | The values shall be based on the same cables and conditions of the test for resistance to electromechanical forces specified in IEC 61914.
| conforming with EGAT requirement (IEC 61914) |  |  | Trefoil
| Other |  |  | Flat
Metallic
| Composite |  |  | X

## AB16_cleat_Flat-Norma (hidden)
CABLE CLEATS
PD 326.CC
[10 empty] | Dec.2024 | [5 empty] | รายการตรวจ Cable cleat
PROPOSAL DATA | [11 empty] | comment |  |  | 1 | Material
PROCUREMENT REFERENCE |  |  | TIEC-S-06 |  | SCHEDULE NO. |  |  | 1AB16 |  |  |  | waiting for discussion with P'Ja |  |  |  | 1.1 | Metallic: | ALUMINUM 5000 SERIES
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB16-3 | [10 empty] | SS316L Stainless steel
[16 empty] | 1.2 | Composite:
[18 empty] | Metalic part | ALUMINUM 5000 SERIES
SS316L Stainless steel
a. | Manufacturer and Country of Origin | [16 empty] | non-metallic part | ANY
|  | - Manufacturer |  |  | NORMA GROUP
|  | - Country of origin |  |  | China | [9 empty] | 2 | Force/1Cleat must be more than RF EGAT
[12 empty] | ปรับให้พิจารณาแค่ type โดยขนาดของ cleat |  |  |  | 2.1 | FLAT
b. | Type/Model[1] |  |  |  | FF-S3236 | [6 empty] | จะพิจารณาในขั้นบริหารสัญญา | [5 empty] | Calculated result | #REF!
c. | For XLPE Cable Suitability[1] | [10 empty] | ตัดออกเนื่องจากพิจารณาขนาด
| - Overall Diameter Range |  |  |  | Min | 32 | mm. |  | Max | 36 | mm. | ในขั้นบริหารสัญญา
d. | Applied Standard |  |  |  | conforming with EGAT requirement (IEC 61914)
*in case of other, please specify in the box below:
e. | Classification according to material[2] |  |  |  |  | Metallic | [5 empty] | แก้รูปแบบ
Material :
[5 empty] | X | Composite
[6 empty] | Material : | Stainless Steel | [9 empty] | EGAT
[6 empty] | and | Polyolefin | [9 empty] | V | I short circuit | Lineal Spacing | FLAT Force | TREFOIL Force
f. | Resistant to electromechanical forces, withstanding more than one short circuit[3] | [15 empty] | 230 | 170 |  | #REF! | #REF!
| - Cable centre spacing (S) |  |  |  | 35 |  | mm |  |  |  |  | 0.16 | 0.17 | #REF! |  |  |  | Force
| - The peak short circuit current of the 2nd shortcircuit |  |  |  | 125 |  | kA |  |  |  |  | Trefoil wtihstrand force | [5 empty] | #REF!
| - Lineal spacing (D) |  |  |  | 600 |  | mm |  |  |  |  | Flat force withstrand force
g. | Formation |  |  |  | Flat | [6 empty] | ขอย้ายไปด้านบนได้ไหม
| Note [1]: | The exact size of Cable Cleat shall be confirmed after the exact overall diameter of XLPE power cable is confirmed during project stage. | [9 empty] | เพิ่มเพื่อความชัดเจน
| Note [2]: | Definitions comply with IEC 61914. metallic consisting of metal only. composite consisting of metallic and non-metallic materials.
a) Fibre reinforced resin materials are not considered to be composite.
b) Materials include any materials supplied by the manufacturer as part of a cable cleat or intermediate restraint or with a cable cleat or intermediate restraint in the same packaging. This may include fixings such as nuts, bolts, screws, washers, springs and pins.
| Note [3]: | The data specified in this item shall conform to the Type Test Report of the type proposed.
| Note [4]: | The values shall be based on the same cables and conditions of the test for resistance to electromechanical forces specified in IEC 61914.
| conforming with EGAT requirement (IEC 61914) |  |  | Trefoil
| Other |  |  | Flat
Metallic
| Composite |  |  | X

## AB17_XLPE-Bangkok Cable (hidden)
115 kV and below XLPE POWER CABLE
FORM PD 322
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB17
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB17-1
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  |  | Bangkok Cable Co., Ltd.
|  | - Country of origin |  |  | Thailand
b. | Type / Model / Cat. NO. |  |  |  | CV(TS)
c. | Applied Standard |  |  |  | conforming with EGAT requirement ( ICEA Pub. No S-93-639)
*in case of other, please specify in the box below :
d. | Voltage Class |  |  |  | 25 |  |  |  |  | kV
e. | Calculated Cross-Sectional Area of Stranded Conductor |  |  |  | 35.7 |  |  |  |  | mm2
|  | - Material of Conductor |  |  | Copper
|  | - No. of Wires in the Stranded Conductor |  |  | 7
|  | - Diameter of Each Wire |  |  | 2.65 |  |  |  |  | mm
f. | Outside Diameter of Stranded Conductor |  |  |  | Min | 6.88 | mm |  | Max | 7.02 | mm
g. | Conductor Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.6 | mm
h. | Insulation |  | (Material / Thickness) |  | XLPE |  |  |  | / | 8.76 | mm
i. | Insulation Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.7 | mm
j. | Outside Diameter of Insulation with |  |  |  | Min | 25.5 | mm |  | Max | 27.5 | mm
Extruded Semi-Conducting Insulation Screen (min-max)
k. | Metal Screen/Sheath |  | (Material / Thickness) |  | Copper tape |  |  |  | / | 0.1 | mm
l. | Cushion |  | (Material / Thickness) |  | Polyester Non-woven Tape |  |  |  | / | 0.1 | mm
m. | Oversheath (Jacket) |  | (Material / Thickness) |  | PVC |  |  |  | / | 2.03 | mm
n. | Overall Diameter (min-max) |  |  |  | Min | 31 | mm |  | Max | 35 | mm
o. | Impulse Withstand Voltage (BIL) |  |  |  | 150 | [5 empty] | kV
p. | (1) Ampacity of conductor in Free Air, Flat Formation with Spacing 1 Time Diameter [1] | [7 empty] | 200 |  | A
| (2) Ampacity of conductor for Direct Burial, Flat Formation with Spacing 1 Time Diameter, | [7 empty] | 160 |  | A
Depth of Laying in Ground 0.4 m, Soil Thermal Resistivity 1.2°C-m/watt [1]
q. | Min Bending Radius as a Multiple of Cable Diameter
|  | - During installation |  |  | 10 |  |  |  |  | Times
|  | - After Installation |  |  | 10 |  |  |  |  | Times
r. | Max Resistance at 20 °C of Conductor |  |  |  | 0.524 |  |  |  |  | Ω/km
s. | Length of Cable per Reel |  |  |  | 500 |  |  |  |  | m
Note [1]: |  | Conductor Temperature not in Excess of 90°C at 100% Load Factor and at an Ambient Temperature of 45°C
Note [2]: |  | Drawing and dimension of Cable Reels/Drums together with packing details shall be submitted during project stage for EGAT approval.
conforming with EGAT requirement ( ICEA Pub. No S-93-639)
conforming with EGAT requirement (TIS 2202)
conforming with EGAT requirement (IEC 62067)
Other*

## AB17_XLPE-Yazaki (hidden)
115 kV and below XLPE POWER CABLE
FORM PD 322
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | TIEC-S-06 | SCHEDULE NO. |  |  | 1AB17
BIDDER |  | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB17-1
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  |  | THAI-YAZAKI ELECTRIC WIRE CO., LTD.
|  | - Country of origin |  |  | THAILAND
b. | Type / Model / Cat. NO. |  |  |  | 25KV-CV (EGAT) / 1 x 35 mm²
c. | Applied Standard |  |  |  | conforming with EGAT requirement ( ICEA Pub. No S-93-639)
*in case of other, please specify in the box below :
IEC 60228
d. | Voltage Class |  |  |  | 25 |  |  |  |  | kV
e. | Calculated Cross-Sectional Area of Stranded Conductor |  |  |  | Approx. 33.83 |  |  |  |  | mm2
|  | - Material of Conductor |  |  | COPPER
|  | - No. of Wires in the Stranded Conductor |  |  | 7
|  | - Diameter of Each Wire |  |  | Approx. 2.65 |  |  |  |  | mm
f. | Outside Diameter of Stranded Conductor |  |  |  | Min | 6.84 | mm |  | Max | 6.97 | mm
g. | Conductor Screen |  | (Material / Thickness) |  | Semi-conducting compound |  |  |  | / | Approx. 0.6 | mm
h. | Insulation |  | (Material / Thickness) |  | XLPE |  |  |  | / | 8.76 | mm
i. | Insulation Screen |  | (Material / Thickness) |  | Semi-conducting compound |  |  |  | / | Approx. 0.6 | mm
j. | Outside Diameter of Insulation with |  |  |  | Min | 26.9 | mm |  | Max | 28.3 | mm
Extruded Semi-Conducting Insulation Screen (min-max)
k. | Metal Screen/Sheath |  | (Material / Thickness) |  | Annealed copper tape |  |  |  | / | Approx. 0.1 | mm
l. | Cushion |  | (Material / Thickness) |  | Polyester non-woven tape |  |  |  | / | Approx. 0.24 | mm
m. | Oversheath (Jacket) |  | (Material / Thickness) |  | PVC |  |  |  | / | 1.78 | mm
n. | Overall Diameter (min-max) |  |  |  | Min | 31 | mm |  | Max | 35 | mm
o. | Impulse Withstand Voltage (BIL) |  |  |  | 150 | [5 empty] | kV
p. | (1) Ampacity of conductor in Free Air, Flat Formation with Spacing 1 Time Diameter [1] | [7 empty] | 202 |  | A
| (2) Ampacity of conductor for Direct Burial, Flat Formation with Spacing 1 Time Diameter, | [7 empty] | 180 |  | A
Depth of Laying in Ground 0.4 m, Soil Thermal Resistivity 1.2°C-m/watt [1]
q. | Min Bending Radius as a Multiple of Cable Diameter
|  | - During installation |  |  | 10D |  |  |  |  | Times
|  | - After Installation |  |  | 10D |  |  |  |  | Times
r. | Max Resistance at 20 °C of Conductor |  |  |  | 0.524 |  |  |  |  | Ω/km
s. | Length of Cable per Reel |  |  |  | 500 |  |  |  |  | m
Note [1]: |  | Conductor Temperature not in Excess of 90°C at 100% Load Factor and at an Ambient Temperature of 45°C
Note [2]: |  | Drawing and dimension of Cable Reels/Drums together with packing details shall be submitted during project stage for EGAT approval.
conforming with EGAT requirement ( ICEA Pub. No S-93-639)
conforming with EGAT requirement (TIS 2202)
conforming with EGAT requirement (IEC 62067)
Other*

## AB18_LV_Turnkey-Bangkok Cable
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD AB18
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. | 1AB18, 2AB18, 3AB18, 4AB18
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB18-1 thru 1AB18-6, 2AB18-1 thru 2AB18-7, 3AB18-1 thru 3AB18-4, 4AB18-1 thru 4AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2559) |  | conforming with EGAT requirement (TIS838-2531)
*in case of other, please specify in the box below :
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
|  | - Manufacturer |  | Bangkok Cable Co., Ltd. |  |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand |  |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2553) |  |  | conforming with EGAT requirement (TIS11-2559)
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B3, ASTM B8)
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | Sinthani Industry Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM A363)
*in case of other, please specify in the box below :
e. | Aluminum Conductor
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B231, ASTM B232)
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other

## AB18_LV_Turnkey-Yazaki
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD AB18
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. | 1AB18, 2AB18, 3AB18, 4AB18
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB18-1 thru 1AB18-6, 2AB18-1 thru 2AB18-7, 3AB18-1 thru 3AB18-4, 4AB18-1 thru 4AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
|  | - Manufacturer |  | THAI-YAZAKI ELECTRIC WIRE CO.,LTD.
|  | - Country |  | THAILAND
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2559) |  | conforming with EGAT requirement (TIS838-2531)
*in case of other, please specify in the box below :
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
|  | - Manufacturer |  | THAI-YAZAKI ELECTRIC WIRE CO.,LTD. |  |  | THAI-YAZAKI ELECTRIC WIRE CO.,LTD.
|  | - Country |  | THAILAND |  |  | THAILAND
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2553) |  |  | conforming with EGAT requirement (TIS11-2559)
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
|  | - Manufacturer |  | THAI-YAZAKI ELECTRIC WIRE CO.,LTD.
|  | - Country |  | THAILAND
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B3, ASTM B8)
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | THAI-YAZAKI ELECTRIC WIRE CO.,LTD.
|  | - Country |  | THAILAND
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM A363)
*in case of other, please specify in the box below :
e. | Aluminum Conductor
|  | - Manufacturer |  | THAI-YAZAKI ELECTRIC WIRE CO.,LTD.
|  | - Country |  | THAILAND
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B231, ASTM B232)
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other

## AB19_Flood LED-Racer (hidden)
LED FLOOD LIGHTING FIXTURE
FORM PD 611.1(L)
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. | 1AB19, 2AB19, 4AB19
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB19-1, 2AB19-1, 4AB19-1
a. | Applied Standards |  |  | Conform to EGAT specification
b. | Lighting Fixture
| - Manufacturer / Country |  |  | Racer / Thailand
| - Type / Model / Cat. No. |  |  | FINXI-I 100W
- Material
|  | - Housing |  | Die cact aluminium
|  | - Front Cover |  | Polycabonete
|  | - Mounting Bracket |  | Steel sa Galvanize plating
| - Degree of protection |  |  | IP65
| - Dimension (approx.) |  |  | 310W*365L*60H (+-5) |  | mm
| - Weight (approx.) |  |  | 3.80 (+-0.5) |  | kg
c. | LED
| - Power |  |  | 100 |  | W
| - Color Rendering Index (CRI) |  |  | >70
| - Correlated Color Temperature (CCT) |  |  | 6500 |  | K
d. | Driver
| - Rated Voltage / Frequency / Watt |  |  | 220/50/100 |  | V/Hz/W
| - Power Factor |  |  | >95
e. | Luminaire Efficacy |  |  | 120 |  | lm/W
f. | Service Life |  |  | 50000 |  | h

## AB19_SOLAR Street LED-Racer (hidden)
SOLAR LIGHTING FIXTURE FOR FENCE AND ACCESS ROAD
FORM PD 611.2(S)
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. | 1AB19, 2AB19
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB19-2, 2AB19-2
a. | Applied Standards |  |  | Conform to EGAT Rating and Feature (RF)
b. | Lighting Fixture
| - Manufacturer / Country |  |  | Racer / Thailand
| - Type / Model / Cat. No. |  |  | KELLI-RC40W
- Material
|  | - Housing |  | Corrosion resistant die cast aluminum alloy
|  | - Front Cover |  | Clear Poly-Carbonate
| - Degree of protection |  |  | IP65
| - Adjustable angle of the Housing |  |  | 150*55 |  | degrees
| - Dimension (approx.) |  |  | 1097L*392W*201H (+-10) |  | mm
| - Weight (approx.) |  |  | 10.5 (+-10) |  | kg
c. | LED
| - Luminous Flux |  |  | 6600 |  | lumens
| - Luminaire Efficacy |  |  | 165 |  | lumen/W
- Color Rendering Index (CRI)
| - Correlated Color Temperature (CCT) |  |  | 5700 |  | K
| - Service Life |  |  | 50000 |  | h
d. | Charger
| - Type |  |  | MPPT
| - Voltage |  |  | 12 |  | Vdc
| - Ampacity |  |  | 10 |  | A
e. | Solar Panel
| - Type |  |  | Monocrystalline
| - Power |  |  | 80 |  | W
| - Voltage |  |  | 18 |  | V
f. | Battery
| - Type |  |  | LiFePO4
| - Capacity |  |  | 30 |  | Ah
| - Voltage |  |  | 12.8 |  | V
| - Battery Backup Time |  |  | 15 |  | h
| - Full charge Time |  |  | 5 |  | h
*in case of other, please specify in the box below :

## AB19_Lamp post-Racer (hidden)
TAPERED GALVANIZED STEEL LAMP POST
FORM PD 611.1
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. | 1AB19, 2AB19
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB19-3, 2AB19-3
a. | Manufacturer / Country
| - Fabrication |  |  | Racer Electric(Thailand)Co.,Ltd/Thailand
| - Hot Dip Galvanizing |  |  | Siam steel Galvanizing Co.,Ltd/Thailand
b. | Applied Standards
| - Structural Steel |  |  | TIS1479-2558
| - Anchor Bolt and Nut |  |  | JIS B 1178/ASTM A325
| - Washer |  |  | -
| - Hot Dip Galvanizing |  |  | ASTM A123/A 123M-13

## AB20_AT,CN&MH (hidden)
ALUMINUM TUBE, CONNECTOR AND MISCELLANEOUS HARDWARE
FORM PD-AB20
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB20, 2AB20, 3AB20, 4AB20
BIDDER |  | IN CONSORTIUM |  | ITEM NO. |  | 1AB20-1 thru 1AB20-5, 2AB20-1, 2AB20-2, 3AB20-1, 3AB20-2, 4AB20-1 thru 4AB20-3
a. | Aluminum Tube
| - Manufacturer / Country |  |  | ALMET THAI LIMITED.
| - Applied Standards |  |  | X | ASTM B241
| - Aluminum Alloy Designation and Temper |  |  | Alcan Alloy 50S-T6 equivalent AA 6063 - T6
b. | 500 kV Compression Connector
| - Manufacturer / Country |  |  | Preformed Line Products (Thailand) Ltd./ Thailand
| - Applied Standards |  |  | X | NEMA CC1
| - Aluminum Alloy Designation and Temper |  |  | 1050 T1
| - Compression Dead End Body |  |  | X | Extruded Tube |  | Casting
| - Compression Terminal Body |  |  | X | Extruded Tube |  | Casting
| - Compression Connector Body |  |  | X | Extruded Tube |  | Casting
c. | 230 kV and below Compression Connector
| - Manufacturer / Country |  |  | Preformed Line Products (Thailand) Ltd./ Thailand
| - Applied Standards |  |  | X | NEMA CC1
| - Aluminum Alloy Designation and Temper |  |  | 1050 T1
| - Compression Dead End Body |  |  | X | Extruded Tube |  | Casting
| - Compression Terminal Body |  |  | X | Extruded Tube |  | Casting
| - Compression Connector Body |  |  | X | Extruded Tube |  | Casting
d. | 500 kV Miscellaneous Hardware
| - Manufacturer / Country |  |  | Preformed Line Products (Thailand) Ltd. / Thailand
e. | 230 kV and below Miscellaneous Hardware
| - Manufacturer / Country |  |  | Preformed Line Products (Thailand) Ltd. / Thailand
Note. Drawings of the following equipment shall be submitted for preliminary consideration. Actual type (such as size, length etc.) shall be submitted for approval after design stage.
- Aluminum Tube - Compression Connector - Miscellaneous Hardware

## AB21_BF_EPC (hidden)
BUS FITTING
FORM PD-AB21
Nov. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB21, 2AB21, 3AB21, 4AB21
BIDDER | IN CONSORTIUM |  |  | ITEM NO. |  | 1AB21-1, 1AB21-2, 2AB21-1, 3AB21-1, 4AB21-1
a. 500 kV Bus Fitting
| Manufacturer / Country |  |  | Subcon / Austria
| Applied Standards |  |  | X | NEMA CC1
| Aluminum Alloy Designation and Temper |  |  | Alsi7Mg0,3 T6
Hardware
- Aluminum
|  | - Bolts Alloy and Temper |  | A280
|  | - Nuts Alloy and Temper |  | A280
|  | - Split Lock Washer Alloy and Temper |  | A280
|  | - Anodic Coating and Lubricate |  | X | Yes | No
- Stainless Steel
|  | - Bolts Alloy No. |  | -
|  | - Nuts Alloy No. |  | -
|  | - Flat Washer Alloy No. |  | -
|  | - Belleville Washers Alloy No. |  | -
b. 230 kV and below Bus Fitting
| Manufacturer / Country |  |  | Preformed Line Products (Thailand) Ltd. / Thailand
| Applied Standards |  |  | X | NEMA CC1
| Aluminum Alloy Designation and Temper |  |  | CC401 (LM6), A356
Hardware
- Aluminum
|  | - Bolts Alloy and Temper |  | -
|  | - Nuts Alloy and Temper |  | -
|  | - Split Lock Washer Alloy and Temper |  | -
|  | - Anodic Coating and Lubricate |  |  | Yes | No
- Stainless Steel
|  | - Bolts Alloy No. |  | STAINLESS STEEL GRADE 304
|  | - Nuts Alloy No. |  | STAINLESS STEEL GRADE 304
|  | - Flat Washer Alloy No. |  | STAINLESS STEEL GRADE 304
|  | - Belleville Washers Alloy No. |  | STAINLESS STEEL GRADE A2/80
Note. Drawings of bus fitting shall be submitted for preliminary consideration. Actual type (such as size, length etc.) shall be submitted for approval after design stage.

## AB22_GM_EPC (hidden)
GROUNDING MATERIAL
FORM PD AB22
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. | 1AB22, 2AB22, 3AB22, 4AB22
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB22-1 thru 1AB22-5, 2AB22-1 thru 1AB22-3, 3AB22-1 thru 3AB22-3, 4AB22-1 thru 4AB22-2
a. | Manufacturer / Country
|  | - Ground Rod |  | KUMWELL CORPORATION PCL../Thailand (KUMWELL)
|  | - Thermite Welding Material |  | KUMWELL CORPORATION PCL../Thailand (KUMWELL)
|  | - Grounding Hardware |  | KUMWELL CORPORATION PCL../Thailand (KUMWELL)
|  | - Disconnecting Switch Safety Mat |  | KUMWELL CORPORATION PCL../Thailand (KUMWELL)
|  | - Maintenance Grounding Connector and |  | ARCUS Elektrotechnik Alois Schiffmann GmbH / Germany
Guide, Bus Connector, Earthing and
Shorting Circuit Cable (500 kV)
|  | - Grounding Tool Equipment, Portable Ground |  | ARCUS Elektrotechnik Alois Schiffmann GmbH / Germany
Attachment Rod and Clamp (500 kV)
|  | - Portable Temporary Grounding Tools |  | ARCUS / Germany, Hubbell Power System / USA
for Maintenance
b. | Detail of Ground Rod
|  | - Applied Standards |  | UL 467
|  | - Material |  | Copper bond Steel
|  | - Method of Production |  | Electro Plating
|  | - Copper Coating Thickness (min.) |  | 0.254 |  | mm
Note. Catalog of the following equipment shall be submitted for preliminary consideration. Actual type (such as size, length etc.) shall be submitted for approval after design stage.
- | Ground Rod
- | Thermite Welding Material
- | Grounding Hardware
- | Disconnecting Switch Safety Mat
- | Maintenance Grounding Connector and Guide, Bus Connector, Earthing and Shorting Circuit Cable (500 kV)
- | Grounding Tool Equipment, Portable Ground Attachment Rod and Clamp (500 kV)
- | Portable Temporary Grounding Tools for Maintenance

## AB23__EPC (hidden)
SUBSTATION MISCELLANEOUS
FORM PD AB23
Mar. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. | 1AB23
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB23-1 to 1AB23-5
a. | Manufacturer / Country
| - Rigid Steel Conduit |  |  | PAT or RSI or Arrow / Thailand
| - Fittings for Rigid Steel Conduit |  |  | Steel City or Abso / Thailand
| - HDPE Conduit |  |  | TGG or TAP or TFOC / Thailand
| - Fittings For HDPE Conduit |  |  | TGG or TAP or TFOC / Thailand
| - Heat Shrinkable Insulation Material |  |  | Raychem / Germany
(For Medium Voltage)
Note. Catalog of the following equipment shall be submitted for preliminary consideration. Actual type (such as size, length etc.) shall be submitted for approval after design stage.
| - | Rigid Steel Conduit and fittings
| - | HDPE Conduit and fittings
| - | Heat Shrinkable Insulation Material

## Cover (1) (hidden)
Proposal Data |  | Instruction
Cover page |  | Proposal Data
Bidder name: | IN CONSORTIUM | Name: | Power Circuit Breaker
Bid No: | TIEC-S-06
* If more than one type of equipment is proposed per one proposal data, the bidder shall create additional Excel sheets. For example, if two types of auxiliary relays are used, there must be two PD-16 sheets.
**Please fill in blue cell
ตัวอย่าง
|  | No. | Specification Detail | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark
|  | a. | Make and country of origin
- Circuit breaker
|  |  | - Make | Digit
|  |  | - Country of origin | Digit
- Steel support structure
|  |  | - Make | Digit
|  |  | - Country of origin | Digit
|  | b. | Type
|  |  | - Interupting Medium (SF6, Vacuum, etc) | Digit
|  |  | - Tripping (Three Poles) | YES NO
|  |  | - Tripping (Single pole & Three poles) | YES NO
|  | f. | Rated voltage
|  |  |  | Digit | kV
|  | s. | Control voltage rating
|  |  | - Normal voltage (From) (min) | Digit | Vdc |  | 10
|  |  | - Normal voltage (From) (max) | Digit | Vdc |  | 20
|  |  | - Normal voltage (To) (min) | Digit | Vdc |  | 30
|  |  | - Normal voltage (To) (max) | Digit | Vdc |  | 40
|  |  | - Operation voltage range (min) | Digit | Vdc |  | 100
|  |  | - Operation voltage range (max) | Digit | Vdc |  | 200
|  | A1 | Tower Type:
|  | A1.1 | DAI
|  | A1.1.1 | Basic Body | Text
|  | A1.1.2 | Body Extension | Text
|  | A1.1.3 | Tower Height (m.) | Digit | m. | Ex. 1 -7
กรณีเป็น Row ที่ Bidder กรอก โดยให้สามารถกรอก Format Type เป็น
- Digit
- Text
- Yes No
*หน่วยงานต้องมีการปรับ Template ให้สอดคล้องกับ Template มาตรฐาน
กรณีที่ต้องการเพิ่มคำอธิบายให้ Bidder
(ถ้ามี)
กรอกค่า Benchmark ที่ต้องการให้ระบบทำการเปรียบเทียบ เมื่อมีการเปิดซองและทำการเปรียบเทียบข้อมูลทางเทคนิค
File Format เพื่อนำเข้าสู่ระบบ Excel
กรอกหัวข้อ

## PD-01 1-1 (W&Var TDR-Nov2024)-1 (hidden)
Proposal Data
PD 01 (1/1)
COMBINED WATT & VAR TRANSDUCERS
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ISKRA
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark Spec | Remark
a. | Country of Origin | Slovenia | Text
b. | Applied Standards | IEC 60688 (Pls. see more details as data sheet) | Text
c. | Type | MT440 | Text
d. | Number of Elements | 3 | Digit
e. | Auxiliary Power Supply Input [VDC] | 48-276VAC & 20-300 VDC | Digit
f. | Rated Output Range [mA] | Programmable : 0…1mA or 4…20mA | Digit
g. | Burden :
| - Voltage Circuit per Element [VA] | U2/3.3MOhm : (115x115)/(3.3MOhm)=0.004 | Digit
| - Current Circuit per Element [VA] | I2/0.01Ohm : (20mAx20mA)/0.01 = 0.40 | Digit
h. | Overload Withstand Continuous :
| - Voltage Circuit [%] | 120% ( 600VL-N of 500VL-N ) | Digit
| - Current Circuit [%] | 300% ( 15A of 5A) | Digit
i. | External Resistance Load [kꭥ] | 10V/1mA = 10kOhm & 10V/20mA = 0.5kOhm | Digit
j. | Output Ripple [%] | < 1% P.P. | Digit
k. | Response Time [sec] | < 0.1 | Digit
l. | Calibrate Adjustment [%] | '+/- 5% | Digit
m. | Zero Adjustment [%] | +/- 5% | Digit
n. | Accuracy [%] | 0.5% | Digit
**Please fill in blue cell

## PD-02 1-1 (V TDR-Nov 2024)-1 (hidden)
Proposal Data
PD 02 (1/1)
VOLTAGE TRANSDUCER
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ISKRA
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark Spec | Remark
a. | Country of Origin | Slovenia | Text
b. | Applied Standards | 'IEC 60688 (Pls. see more details as data sheet) | Text
c. | Auxiliary Power Supply Input [VDC] | '48-276VAC & 20-300 VDC | Digit
d. | Voltage Transducer without Suppressed Zero, Voltage Type :
| - Type | MT416 | Text
| - Rated Output Range [mA] | Programmable : 0…1mA or 4…20mA | Digit
| - Burden [VA] | U2 /500kOhm | Digit
| - Overload Withstand Continuous [%] | 120% ( 600VL-N of 500VL-N ) | Digit
| - External Resistance Load [kꭥ] | 10V/1mA = 10kOhm & 10V/20mA = 0.5kOhm | Digit
| - Calibrate Adjustment [%] | +/- 5% | Digit
e. | Voltage Transducer with Suppressed Zero or Expanded-Scale, Voltage Type :
| - Type | MT416 | Text
| - Rated Voltage Input [VAC] | 500 VL-N | Digit
| - Specify PT Ratio Range | Programmable : such as 500kV/115V | Digit
| - Suppressed Zero Adjustment Range [VAC] | Programmable : such as 0…85…150V | Digit
| - Input Span Adjustment [VAC] | Programmable : such as 0…150V | Digit
| - Rated Output Range [mA] | Programmable : 0…1mA or 4…20mA | Digit
| - Burden [VA] | U2 /500kOhm : (115x115V)/500kOhm = 0.03 | Digit
| - Overload Withstand Continuous [VAC] | 120% ( 600VL-N of | Digit
| - External Resistance Load [kꭥ] | 10V/1mA = 10kOhm & 10V/20mA = 0.5kOhm | Digit
| - Calibrate Adjustment [%] | +/- 5% | Digit
f. | Output Ripple [%] | < 1% P.P. | Digit
g. | Accuracy [%] | 0.5% | Digit
**Please fill in blue cell

## PD-03 1-1 (A TDR-Nov 2024)-1 (hidden)
Proposal Data
PD 03 (1/1)
CURRENT TRANSDUCER
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ISKRA
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark Spec | Remark
a. | Country of Origin | Slovenia | Text
b. | Applied Standards | IEC 60688 (Pls. see more details as data sheet) | Text
c. | Type | MT418 | Text
d. | Auxiliary Power Supply Input [VDC] | 48-276VAC & 20-300 VDC | Digit
e. | Rated Current Input [A] | [ ] 1A only [ ] 5A only [ /] settable 1 or 5A | Digit
f. | Rated Output Range [mA] | Programmable : 0…1mA or 4…20mA | Digit
g. | Burden [VA] | I2/0.01Ohm : (20mAx20mA)/0.01 = 0.40 | Digit
h. | Overload Withstand Continuous [%] | 300% ( 15A of 15A) | Digit
i. | External Resistance Load [kꭥ] | 10V/1mA = 10kOhm & 10V/20mA = 0.5kOhm | Digit
j. | Calibrate Adjustment [%] | +/- 5% | Digit
k. | Output Ripple [%] | < 1% P.P. | Digit
l. | Accuracy [%] | 0.5% | Digit
**Please fill in blue cell

## PD-04 1-1 (T TDR-Nov 2024)-1 (hidden)
Proposal Data
PD 04 (1/1)
TEMPERATURE TRANSDUCER
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ISKRA
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark Spec | Benmark
a. | Country of Origin | Slovenia | Text
b. | Applied Standards | IEC 60770-1 (Please see more details as data sheet) | Text
c. | Type | MI450 | Text
d. | Specify Input RTD Sensor Type | Programmable : Pt100 , Cu10 , Ni100
e. | Temperature Range [°C] | Programmable : Such as 20 - 140 C deg. | Digit
f. | Rated Output [mA] | Programmable : 0…1mA or 4…20mA | Digit
g. | External Load Resistance [kꭥ] | 15V/1mA = 15 kOhm & 15V/20mA = 0.75 kOhm | Digit
h. | Accuracy [%] | All RTD Sensor 0.5% (Except Cu10 = 1 %) | Digit
i. | Response Time [sec] | 0.5 Sec | Digit
j. | Calibrate Adjustment [%] | Programmable +/- 5% | Digit
k. | Zero Adjustment [%] | Programmable +/- 5% | Digit
**Please fill in blue cell

## PD-05 1-1 (SYNC-Nov 2024)-1 (hidden)
Proposal Data
PD 05 (1/1)
SYNCHRONIZING PANEL
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ISKRA
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | Benmark Spec | Benmark
a. | Conutry of Origin | Slovenia | Text
b. | Applied Standards | 60051-1, 60529, 61010-1, 61326, UL94 V-0 | Text
c. | Indicating Voltmeter for Incoming and Running Potentials :
| - Manufacturer | Iskra | Text
| - Conutry of Origin | Slovenia | Text
| - Type | FQ1108 | Text
| - Type of Scale [V] | 2 x 50 V | Digit | V
| - Operation Principle | Moving - Iron | Text
| - Burden at Rated Voltage [VA] | 4 VA | Digit | VA
| - Accuracy Class [%] | 1.5 % | Digit | %
| - Response Time [sec] | - | Digit | sec
| - Overload Rating Continuous [%] | - | Digit | %
d. | Indicating Frequency Meter for Incoming and Running Frequencies :
| - Manufacturer | Iskra | Text
| - Conutry of Origin | Slovenia | Text
| - Type | ZQ1108 | Text
| - Type of Scale | 2 x 45 - 55 Hz | Text
| - Operation Principle | Moving - Coil | Text
| - Burden at Rated Voltage [VA] | 0.24 VA | Digit | VA
| - Accuracy Class [+/- Hz] | 0.5 | Digit | +Hz
| - Response Time [sec] | - | Digit | sec
| - Overload Rating Continuous [%] | - | Digit | %
e. | Synchroscope :
| - Manufacturer | Iskra | Text
| - Conutry of Origin | Slovenia | Text
| - Type | SQ0104 | Text
| - Type of Scale | Circular set of 24 LEDs | Digit
| - Operation Principle | Phase Difference | Text
- Burden at Rated Voltage :
| - Running [VA] | 4 VA | Digit | VA
| - Incoming [VA] | 4 VA | Digit | VA
| - Accuracy Class [%] | +- 3 Deg el | Digit | %
| - Response Time [sec] | 300 ms | Digit | sec
**Please fill in blue cell

## PD-16 1-1 (94-Nov 2024)-1 (hidden)
Proposal Data
PD 16 (1/1)
AUXILIARY TRIPPING RELAYS
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ARTECHE
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | Benmark
a. | Country of Origin | SPAIN | Text
b. | Applied Standards | IEC | Text
c. | Type | AUXILIARY TRIPPING RELAYS | Text
d. | Is the Tripping Relay High Burden Type? | [ X ] Yes [ ] No | Yes No
e. | Time to Stable Closing [ms] | <8 ms (Including Bouncing Time) | Digit | ms
| Operating Time [ms] | <8 ms (Including Bouncing Time) | Digit | ms
| Bouncing Time [ms] | <3 ms | Digit | ms
f. | Output Contacts Rating at 125 VDC
| Make and carry 300V for 3 second [A] | 30A for 3 Sec for 9000W Max. | Digit | A
| Make and carry 300V continuously [A] | continueous current 10A | Digit | A
| Break for inductive current (L/R £40 ms) [A] | 0.52 A for 50,000 operations | Digit | A
g. | DC Voltage Rating [A] | 125 VDC | Digit | V
| Operative Voltage Range [V] | +10%/-20% Un at the extreme temperature condition. | Digit | V
h. | Number of Electrically Separate NO. & CO. Contacts
| Model | RJ-8R HB | Text
| -NO | 8 | Digit
| -CO | 8 | Digit
| Model | RJ-16R HB | Text
| -NO | 16 | Digit
| -CO | 16 | Digit
| Model |  | Text
| -NO |  | Digit
| -CO |  | Digit
| Model |  | Text
| -NO |  | Digit
| -CO |  | Digit
**Please fill in blue cell

## PD-17 1-1 (86-Nov 2024)-1 (hidden)
Proposal Data
PD 17 (1/1)
AUXILIARY TRIPPING AND LOCKOUT RELAYS
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | MORSMITT
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | Benmark
a. | Country of Origin | Australia | Text
b. | Applied Standards | IEC | Text
c. | Type | 6RJ25 | Text
d. | Is the Lockout Relay High Burden Type? | [ / ] Yes [ ] No | Yes No
e. | Is the Lockout Relay reset by Hand and Electrically? | [ / ] Yes [ ] No | Yes No
f. | Is the Cut-Off Contact provided to interrupt | [ ] Yes [ ] No | Yes No
the Operating Coil ?
g. | Time to stable closing [ms] | N/A | Digit | ms
| Operating Time [ms] | <10 ms | Digit | ms
| Bouncing Time [ms] | N/A | Digit | ms
h. | Output Contacts rating at 125 VDC
| Make and carry 300V for 3 second [A] | 7500 VA (ac) or 7500 W (dc) _ A | Digit | A
| Make and carry 300V continuously [A] | 3000 VA (ac) or 3000 W (dc) _ A | Digit | A
| Break for inductive current (L/R £40 ms) [A] | 3000 VA (ac) or 62.5 W resistive (dc) or 31.25W inductive (dc) | Digit | A
i. | DC Voltage rating [V] | 125 _V | Digit | V
| Operative Voltage Range [V] | 81.25V (65%) to 150V (120%) V | Digit | V
j. | Number of Electrically Separate NO., NC. & CO. Contacts
| Model | 6RJ25-10-E-8M2B | Text
| -NO | 8 | Digit
| -NC | 2 | Digit
| -CO |  | Digit
| Model | 6RJ25-20-E-16M4B | Text
| -NO | 16 | Digit
| -NC | 4 | Digit
| -CO |  | Digit
| Model | 6RJ25-10-E-7M3B | Text
| -NO | 7 | Digit
| -NC | 3 | Digit
| -CO |  | Digit
| Model | 6RJ25-20-E-18M2B | Text
| -NO | 18 | Digit
| -NC | 2 | Digit
| -CO |  | Digit
**Please fill in blue cell

## PD-18.1 1-2 (C&P PNL-Nov2024)-1 (hidden)
Proposal Data | [6 empty] | PANEL ASSEMBLY FOR CONTROL AND PROTECTION SYSTEM
PD 18.1 (1/1)
PANEL ASSEMBLY FOR CONTROL AND PROTECTION SYSTEM | [8 empty] | BIDDER NAME _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | BID NO. _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | SCI ELECTRIC PUBLIC COMPANY LIMITED
MANUFACTURER_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark | a. | Make and Country of Origin |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
a. | Country of Origin | SCI ELECTRIC PUBLIC COMPANY LIMITED | Text |  | b. | Engineering Work |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
[5 empty] | c. | Blank Panel Maker |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
b. | Engineering Work | SIEMENS LIMITED | Text |  | [ ] | I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER).
[5 empty] | d. | Applied Standards
c. | Blank Panel Maker | SCI ELECTRIC PUBLIC COMPANY LIMITED | Text |  |  |  | Dielectric withstand | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
|  | [ X ] I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER) FOR 500kV. |  |  |  |  | Insulation Resistance | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
d. | Applied Standards | [5 empty] | Temperature Range | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Dielectric withstand | 2,000 VAC / 1 s | Digit |  | e. | Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Insulation Resistance | 500 VDC | Digit |  | f. | The thickness of leveled sheet steel and | [ ] Yes | [ ] No
| - Temperature Range [°C] | 25 to 30 C | Digit |  |  | formed steel members is not less than 2.5 mm. |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
e. | Type | INDOOR | Text |  |  | If no, specify the supporting structure method. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
f. | The thickness of leveled sheet steel and | [ X ] Yes [ ] No | Yes No |  | g. | Degree of protection | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| formed steel members is not less than 2.5 mm. |  |  |  | h. | Ambient temperature | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ °C
| If no, specify the supporting structure method. |  | Text |  | i. | Ambient humidity | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ %
g. | Degree of protection | IP 30 | Text |  | j. | Terminal Block
h. | Ambient temperature [°C] | 5-45 C | Digit |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
i. | Ambient humidity [%] | 95 % | Digit |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
j. | Other equipments [Type / Manufacturer] |  |  |  | k. | Miniature Circuit Breaker
| j1. Test switch |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Control and Protection | 2RMLG02 / SIEMENS | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Metering | FT1 / ABB | Text
| j2. Undervoltage Relay | RUT-4 / ARTECHE | Text |  | l. | Switchboard wire
| j3. Terminal Block |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For AC/DC power supply | AVK16RD / KLEMSAN | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For PT and control circuits | AVK10 / KLEMSAN | Text
| - For CT circuits | WGO3 / KLEMSAN | Text |  | m. | Test Equipment
| - For Alarm/Status circuits and marshalling cabinet | AVK4A / KLEMSAN | Text |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j4. Miniature Circuit Breaker | CSMBS / C&S | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j5. Switchboard wire | N/A | Text
[5 empty] | n. | The normal size of drawings. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
k. | Specify type and manufacturer of spectial tool, | N/A | Text |  |  | If not A1, give reason. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| if needed. |  | Text |  | o. | Specify type and manufacturer of spectial tool, | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
**Please fill in blue cell

## PD-18.1 2-2 (C&P PNL-Nov2024)-1 (hidden)
Proposal Data | [6 empty] | PANEL ASSEMBLY FOR CONTROL AND PROTECTION SYSTEM
PD 18.1 (1/1)
PANEL ASSEMBLY FOR CONTROL AND PROTECTION SYSTEM | [8 empty] | BIDDER NAME _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | BID NO. _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | SCI ELECTRIC PUBLIC COMPANY LIMITED
MANUFACTURER_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark | a. | Make and Country of Origin |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
a. | Country of Origin | SCI ELECTRIC PUBLIC COMPANY LIMITED | Text |  | b. | Engineering Work |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
[5 empty] | c. | Blank Panel Maker |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
b. | Engineering Work | SCI ELECTRIC PUBLIC COMPANY LIMITED | Text |  | [ ] | I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER).
[5 empty] | d. | Applied Standards
c. | Blank Panel Maker | SCI ELECTRIC PUBLIC COMPANY LIMITED | Text |  |  |  | Dielectric withstand | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
|  | [ X ] I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER) FOR 230kV. |  |  |  |  | Insulation Resistance | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
d. | Applied Standards | [5 empty] | Temperature Range | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Dielectric withstand | 2,000 VAC / 1 s | Digit |  | e. | Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Insulation Resistance | 500 VDC | Digit |  | f. | The thickness of leveled sheet steel and | [ ] Yes | [ ] No
| - Temperature Range [°C] | 25 to 30 C | Digit |  |  | formed steel members is not less than 2.5 mm. |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
e. | Type | INDOOR | Text |  |  | If no, specify the supporting structure method. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
f. | The thickness of leveled sheet steel and | [ X ] Yes [ ] No | Yes No |  | g. | Degree of protection | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| formed steel members is not less than 2.5 mm. |  |  |  | h. | Ambient temperature | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ °C
| If no, specify the supporting structure method. |  | Text |  | i. | Ambient humidity | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ %
g. | Degree of protection | IP 30 | Text |  | j. | Terminal Block
h. | Ambient temperature [°C] | 5-45 C | Digit |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
i. | Ambient humidity [%] | 95 % | Digit |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
j. | Other equipments [Type / Manufacturer] |  |  |  | k. | Miniature Circuit Breaker
| j1. Test switch |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Control and Protection | 2RMLG02 / SIEMENS | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Metering | FT1 / ABB | Text
| j2. Undervoltage Relay | RUT-4 / ARTECHE | Text |  | l. | Switchboard wire
| j3. Terminal Block |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For AC/DC power supply | AVK16RD / KLEMSAN | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For PT and control circuits | AVK10 / KLEMSAN | Text
| - For CT circuits | WGO3 / KLEMSAN | Text |  | m. | Test Equipment
| - For Alarm/Status circuits and marshalling cabinet | AVK4A / KLEMSAN | Text |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j4. Miniature Circuit Breaker | CSMBS / C&S | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j5. Switchboard wire | N/A | Text
[5 empty] | n. | The normal size of drawings. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
k. | Specify type and manufacturer of spectial tool, | N/A | Text |  |  | If not A1, give reason. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| if needed. |  | Text |  | o. | Specify type and manufacturer of spectial tool, | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
**Please fill in blue cell

## PD-18.2 1-1 (FRS PNL-Nov2024)-1 (hidden)
Proposal Data | [6 empty] | PROPOSAL DATA
PD 18.2 (1/1)
PANEL ASSEMBLY FOR FAULT RECORDING SYSTEM | [6 empty] | PANEL ASSEMBLY FOR FAULT RECORDING SYSTEM
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | SCI ELECTRIC PUBLIC COMPANY LIMITED
[12 empty] | BIDDER NAME _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | BID NO. _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark | MANUFACTURER_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
a. | Country of Origin | THAILAND | Text |  |  |  | a. | Make and Country of Origin |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
[7 empty] | b. | Engineering Work | (FRS Manufacturer) |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
b. | Engineering Work | SIEMENS LIMITED | Text |  |  |  | c. | Blank Panel Maker |  |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
[7 empty] | d. | Applied Standards
c. | Blank Panel Maker | SCI ELECTRIC PUBLIC COMPANY LIMITED | Text | [5 empty] | Dielectric withstand | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
|  | [ / ] I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER). |  |  |  |  | Insulation Resistance | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
d. | Applied Standards | [7 empty] | Temperature Range | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Dielectric withstand | 2,000 VAC / 1s | Digit |  |  |  | e. | Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Insulation Resistance | 500 VDC | Digit |  |  |  | f. | The thickness of leveled sheet steel and | [ ] Yes | [ ] No
| - Temperature Range [°C] | 25 to 30ºC | Digit |  |  |  |  | formed steel members is not less than 2.5 mm.
e. | Type | INDOOR | Text |  |  |  |  | If no, specify the supporting structure method. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
f. | The thickness of leveled sheet steel and | [ / ] Yes [ ] No | Yes No |  |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| formed steel members is not less than 2.5 mm. | [5 empty] | g. | Degree of protection | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| If no, specify the supporting structure method. |  | Text |  |  |  | h. | Ambient temperature | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ °C
g. | Degree of protection | IP30 | Text |  |  |  | i. | Ambient humidity | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ %
h. | Ambient temperature [°C] | 25 TO 30 | Digit | °C |  |  | j. | Terminal Block
i. | Ambient humidity [%] | 50 TO 60 | Digit | % |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
j. | Other equipments [Type / Manufacturer] | [6 empty] | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j1. Test switch | [5 empty] | k. | Miniature Circuit Breaker
| - For Control and Protection | FT-1/ABB | Text |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Metering | N/A | Text
| j2. Undervoltage Relay | N/A | Text |  |  |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j3. Terminal Block | [5 empty] | l. | Switchboard wire
| - For AC/DC power supply | AVK-Series/KLEMSAN | Text |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For PT and control circuits | WGOY6/KLEMSAN | Text
| - For CT circuits | WGOY6/KLEMSAN | Text |  |  |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Alarm/Status circuits and marshalling cabinet | N/A | Text |  |  |  | m. | Test Equipment
| j4. Miniature Circuit Breaker | CSMB /C&S ELECTRIC | Text |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j5. Switchboard wire | N/A | Text
[8 empty] | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
k. | Specify type and manufacturer of spectial tool, | N/A | Text |  |  |  | n. | The normal size of drawings. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| if needed. |  | Text |  |  |  |  | If not A1, give reason. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
**Please fill in blue cell

## PD-19 1-2 (FRS-Nov 2024)-1 (hidden)
Proposal Data
PD 19 (1/2)
FAULT RECORDING SYSTEM
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | SIEMENS
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark
a. | Country of Origin | Germany | Text
b. | Type | 7KE85 | Text
c. | Hardware :
| c1. Type and capacity of hard disk | 16GB | Text
| c2. Easy change every channels between voltage and | [ ] Yes [ X ] No | Yes No
current channels
| If No, give detail |  | Text
| c3. Automatically short CT when remove an analog | [ X ] Yes [ ] No | Yes No
isolator module
| If No, give detail | 24 Bit | Text
| c4. Number of bits for A/D converters |  | Digit
| c5. Have history log or SER log for maintenance | [ X ] Yes [ ] No | Yes No
| c6. Every digital channel shall be start FRS | [ X ] Yes [ ] No | Yes No
independently
| c7. High scan frequency range [Hz] | 1,000 - 6,000 | Digit | Hz
| c8. Slow scan frequency range [Hz] | 1-100 | Digit | Hz
| c9. Dual scan frequency | [ X ] Yes [ ] No | Yes No
| c10. Prefault time [ms] | Fault recorder: 0 to 3 s, programmable in steps of 0.1 sec. Slow scan record(Power/Frequency recorder):0 to 90 sec. | Digit | ms
| c11. Postfault time [ms] | Fault recorder: 1 to 90 s, programmable in step of 0.1 sec. Slow scan recorder (Power/Frequency recorder): 1 t0 90 mins. | Digit | ms
| c12. Event time resolution at least 1 ms | [ X ] Yes [ ] No | Yes No
| c13. Total memory > 32 MB for high scan rate | [ X ] Yes [ ] No | Yes No
| c14. Maximum duration per record at 30 Hz scan rate [min] | Up to 90 | Digit | min
| c15. Duration of working (initialization and reset time) | Approx. <120 Sec. (after switch on device) | Digit | sec
inclusion hardware and software [sec]
| c16. User calculate channel shall be save in | [ X ] Yes [ ] No | Yes No
configuration file
| c17. Continuous self diagnostics (watch dog) | [ X ] Yes [ ] No | Yes No
| If No, give detail |  | Text
d. | Software :
| d1. Number of levels to security access (For User) | Maximum 5 Depending on activation of confirmation IEDs function 1. Setting/operation 2. Operation with function keys and push buttons 3. Switching (process) 4. Switching (unlocked) 5. Switching authority | Text
Detail
| d2. Open many records simultaneously | [ X ] Yes [ ] No | Yes No
| d3. Each channel are displayed on separate axis | [ X ] Yes [ ] No | Yes No
| d4. All waveforms shall be moved to any position | [ X ] Yes [ ] No | Yes No
| d5. Harmonics order |  | Text
| d6. Backup & restore the record with OS command | [ X ] Yes [ ] No | Yes No
(copy & paste)
| If No, give detail |  | Text
| d7. Standard & version of comtrade file | IEC61850 | Text
| d8. Every line shall be calculate power flow | [ X ] Yes [ ] No | Yes No
| d9. Have roll back configuration file when is | [ ] Yes [ X ] No | Yes No
communicating (remote failure)
| d10. Have symbolic windows to indicate a status of | [ X ] Yes [ ] No | Yes No
communication that is success or not
| d11. Polling period | From 1 min to infinity: Time interval is programmable | Digit
| d12. Formula for the channel calculate function | Yes, but function is not programmable. Available in the moment: Differential quotient (DM/Dt), Absolute deviation (DM), Relative deviation(DM/M) in SIGRA | Text
| d13. Combining any record in a new file | [ X ] Yes [ ] No | Yes No
| d14. Print chart same on the monitor | [ X ] Yes [ ] No | Yes No
**Please fill in blue cell

## PD-19 2-2 (FRS-Nov 2024)-1 (hidden)
Proposal Data
PD 19 (2/2)
FAULT RECORDING SYSTEM
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | SIEMENS
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark
e. | Sensor :
e1. Have the starting sensor
| - Overcurrent staring sensor | [ X ] Yes [ ] No | Yes No
| - Undervoltage staring sensor | [ X ] Yes [ ] No | Yes No
| - Frequency staring sensor | [ X ] Yes [ ] No | Yes No
| - Negative sequence voltage starting sensor | [ X ] Yes [ ] No | Yes No
| - Zero sequence voltage starting sensor | [ X ] Yes [ ] No | Yes No
| - Power swing starting sensor | [ X ] Yes [ ] No | Yes No
| - External start | [ X ] Yes [ ] No | Yes No
| e2. Sensor limit operating time [ms] | 1-900 s(15min) in 50 Hz system | Digit | ms
f. | Front Panel :
| Have a keyboard on front panel to set the FRS | [ X ] Yes [ ] No | Yes No
| If No, give detail |  | Text
g. | Panel Assembly :
| Manufacturer | SCI ELECTRIC PUBLIC COMPANY LIMITED | Text
| Country of Origin | THAILAND
h. | Spare parts :
List of all recommended spare parts :
|  | 1.Same ordering number as supplied in schedule 1D25 | Text
|  | 2. | Text
|  | 3. | Text
|  | 4. | Text
|  | 5. | Text
|  | 6. | Text
i. | Service
| i1. Startup with manufacturer’s supervisor | [ X ] Yes [ ] No | Yes No
i2. Service maintenance
| - Response time of the after sale service [Days] | Max.1 Working day | Digit | Days
| - Service respresentative in Thailand | [ X ] Yes [ ] No | Yes No
| i3. 2 years warranty period | [ X ] Yes [ ] No | Yes No
**Please fill in blue cell

## PD-20 1-1 (CO-Nov 2024)-1 (hidden)
Proposal Data
PD 20 (1/1)
CONTROL AND INSTRUMENT SWITCHES
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ESP TECHNOLOGIES LIMITED
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | Benmark
a. | Country of Origin | NOVA / THAILAND | Text
b. | Applied Standards | IEC 60947 | Text
c. | Rated Voltage [V] | 690 V | Digit | V
d. | Breaker Control Switches
| - Type | N/A | Text
| - Color of Handle | N/A | Text
| - Contact Rating Continuous [A] | N/A | Digit | A
| - Is Mechanical Target Provided to Show | [ ] Yes [ ] No | Yes No
the Last Function of the Switch?
e. | Motor-operated Disconnects
| - Type | N/A | Text
| - Color of Handle | N/A | Text
| - Contact Rating Continuous [A] | N/A | Digit | A
| - Is Mechanical Target Provided to Show | [ ] Yes [ ] No | Yes No
the Last Function of the Switch?
f. | Synchronizing Switches
| - Type | N/A | Text
| - Color of Handle | N/A | Text
| - Specify Whether the Handle is | [ ] Yes [ ] No | Yes No
Removable in "OFF" Position Only
g. | Recloser Cutoff Switches
| - Type | NCS-20M2 | Text
| - Color of Handle | OVAL BLACK HANDLE | Text
h. | Trip transfer Switches
| - Type | N/A | Text
| - Color of Handle | N/A | Text
i. | Voltmeter Selector Switches
| - Type | NCS-20M2 | Text
| - Color of Handle | OVAL BLACK HANDLE | Text
j. | Differential Cutoff Switches
| - Type | NCS-20M2 | Text
| - Color of Handle | OVAL BLACK HANDLE | Text
k. | Breaker Failure Cutoff Switches
| - Type | NCS-20M2 | Text
| - Color of Handle | OVAL BLACK HANDLE | Text
l. | Direct Transfer Trip Cutoff Switches
| - Type | NCS-20M2 | Text
| - Color of Handle | OVAL BLACK HANDLE | Text
m. | Permissive Transfer Trip Cutoff Switches
| - Type | NCS-20M2 | Text
| - Color of Handle | OVAL BLACK HANDLE | Text
**Please fill in blue cell

## PD-21(Clearing Time-21-Nov24)-1 (hidden)
Proposal Data
PD 21 (1/1)
TOTAL FAULT CLEARING TIME WITHOUT COMMUNICATION OPERATING TIME FOR 500 kV PROTECTION SYSTEM (DISTANCE RELAY)
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark
a. | Interrupting time of circuit breaker [ms] | A | Digit
b. | Line protection operating time
| b.1 Primary line protection no.1 operating time (b.1-1+b.1-2) [ms] | <18 ms | Digit
| b.1-1 Operating time of distance relay [ms] | <8 ms | Digit
| (Type INGETEAM_EF-ZT) |  | Text
| b.1-2 Operating time of auxiliary tripping relay [ms] | < 10 ms | Digit
| (Type ARTECHE_RJ-16R HB) |  | Text
| b.2 Primary line protection no.2 operating time (b.2-1+b.2-2) [ms] | <18 ms | Digit
| b.2-1 Operating time of distance relay [ms] | <8 ms | Digit
| (Type NR_PCS-902) |  | Text
| b.2-2 Operating time of auxiliary tripping relay [ms] | < 10 ms | Digit
| (Type ARTECHE_RJ-16R HB) |  | Text
c. | Total fault clearing time without communication operating time (a + b)
| c.1 Primary line protection no.1 (a + b.1) [ms] | A + 18 ms | Digit
| c.2 Primary line protection no.2 (a + b.2) [ms] | A + 18 ms | Digit
Note 1 | a. = numerically equal to the sum of opening time and arcing time. The guaranteed interrupting time of circuit breaker shall be verified by the design test record. b.1-1 & b.2-1 = The maximum time which the relay uses to allow signal for the trip command when any fault with the characteristics described in Special Requirement for Total Fault Clearing Time without communication operating time occurs. b.1-2 & b.2-2 = The maximum time which the relay uses to operate itself after receiving the initiated signal from the relay mentioned in b.1-1 & b.2-1.
Note 2 | EGAT shall not accept total fault clearing time without communication operating time exceeding the limitation of 70 ms for the Line Protection with distance relay that is disclosed after commissioning test. The Contractor shall be responsible for all expenses of replacement with new equipment without de-energizing the system.
**Please fill in blue cell

## PD-22(Clearing Time-87-Nov24)-1 (hidden)
Proposal Data
PD 22 (1/1)
TOTAL FAULT CLEARING TIME WITHOUT COMMUNICATION OPERATING TIME FOR 500 kV PROTECTION SYSTEM (LINE DIFFERENTIAL RELAY)
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | Benmark
a. | Interrupting time of circuit breaker |  | Digit | ms
b. | Line protection operating time
| b.1 Primary line protection no.1 operating time (b.1-1+b.1-2) |  | Digit | ms
| b.1-1 Operating time of line differential relay |  | Digit | ms
| (Type_ _ _ _ _ _ _ _ _ _ _ _ _ _) |  | Text
| b.1-2 Operating time of auxiliary tripping relay |  | Digit | ms
| (Type ARTECHE_RJ-16R HB) |  | Text
| b.2 Primary line protection no.2 operating time (b.2-1+b.2-2) |  | Digit | ms
| b.2-1 Operating time of line differential relay |  | Digit | ms
| (Type_ _ _ _ _ _ _ _ _ _ _ _ _ _) |  | Text
| b.2-2 Operating time of auxiliary tripping relay |  | Digit | ms
| (Type ARTECHE_RJ-16R HB) |  | Text
c. | Total fault clearing time without communication operating time (a + b)
| c.1 Primary line protection no.1 (a + b.1) |  | Digit | ms
| c.2 Primary line protection no.2 (a + b.2) |  | Digit | ms
Note 1 | a. = numerically equal to the sum of opening time and arcing time. The guaranteed interrupting time of circuit breaker shall be verified by the design test record. b.1-1 & b.2-1 = The maximum time which the relay uses to allow signal for the trip command when any fault with the characteristics described in Special Requirement for Total Fault Clearing Time without communication operating time occurs. b.1-2 & b.2-2 = The maximum time which the relay uses to operate itself after receiving the initiated signal from the relay mentioned in b.1-1 & b.2-1.
Note 2 | EGAT shall not accept total fault clearing time without communication operating time exceeding the limitation of 80 ms for the Line Protection with line differential relay that is disclosed after commissioning test. The Contractor shall be responsible for all expenses of replacement with new equipment without de-energizing the system.
**Please fill in blue cell

## PD-23(Clearing-21-87-Nov24)-1 (hidden)
Proposal Data
PD 23 (1/1)
TOTAL FAULT CLEARING TIME WITHOUT COMMUNICATION OPERATING TIME FOR 500 kV PROTECTION SYSTEM (LINE DIFFERENTIAL RELAY AND DISTANCE RELAY)
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark
a. | Interrupting time of circuit breaker | A | Digit | ms
b. | Line protection operating time
| b.1 Primary line protection no.1 operating time (b.1-1+b.1-2) | <18 ms | Digit | ms
| b.1-1 Operating time of line differential relay | <8 ms | Digit | ms
| (Type INGETEAM_EF-LD) |  | Text
| b.1-2 Operating time of auxiliary tripping relay | < 10 ms | Digit | ms
| (Type ARTECHE_RJ-16R HB) |  | Text
| b.2 Primary line protection no.2 operating time (b.2-1+b.2-2) | <18 ms | Digit | ms
| b.2-1 Operating time of distance relay | <8 ms | Digit | ms
| (Type INGETEAM_EF-ZT) |  | Text
| b.2-2 Operating time of auxiliary tripping relay | < 10 ms | Digit | ms
| (Type ARTECHE_RJ-16R HB) |  | Text
c. | Total fault clearing time without communication operating time (a + b)
| c.1 Primary line protection no.1 (a + b.1) | A + 18 ms | Digit | ms
| c.2 Primary line protection no.2 (a + b.2) | A + 18 ms | Digit | ms
Note 1 | a. = numerically equal to the sum of opening time and arcing time. The guaranteed interrupting time of circuit breaker shall be verified by the design test record. b.1-1 & b.2-1 = The maximum time which the relay uses to allow signal for the trip command when any fault with the characteristics described in Special Requirement for Total Fault Clearing Time without communication operating time occurs. b.1-2 & b.2-2 = The maximum time which the relay uses to operate itself after receiving the initiated signal from the relay mentioned in b.1-1 & b.2-1.
Note 2 | EGAT shall not accept total fault clearing time without communication operating time exceeding the limitation of 80 ms for the Line Protection with line differential relay and 70 ms for the Line Protection with distance relay that is disclosed after commissioning test. The Contractor shall be responsible for all expenses of replacement with new equipment without de-energizing the system.
**Please fill in blue cell

## PD-24 1-1 (OFC-Nov 2024)-1 (hidden)
Proposal Data
PD 24 (1/1)
OPTIC FIBER CABLE
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | INTERLINK
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | G.652 | OM3
a. | [ X ] Single-mode optical fiber |  |  |  | G.655 | OM4
| 1. Country of origin | China | Text |  |  | OM5
| 2. OFC type | Single mode | Text
| 3. ITU-T Recommendation | G.652D | Text |  | IEC 60793-2-10
| 4. Maximum tensile strength [kg] | 120 | Digit | kg | ITU-T G.651
| 5. Outside diameter [mm] | 11 | Digit | mm | TIA-568.3D
| 6. Maximum weights [kg/km] | 95 ± 10 | Digit | kg/km
| 7. Bending radius [mm] | 220 | Digit | mm
| 8. Optic Fiber Attenuation @ 1310 nm [dB/km] | 0.35 | Digit | db/km
| 9. Optic Fiber Attenuation @ 1550 nm [dB/km] | 0.35 | Digit | db/km
| 10. Dispersion coefficient @ 1310 nm [ps/(nm.km)] | 0.21 | Digit | ps/(nm.km)
| 11. Dispersion coefficient @ 1550 nm [ps/(nm.km)] | 35 | Digit | ps/(nm.km)
12. Maximum splicing loss per point
| - OFC with OPGW [dB] | ≤0.3dB per point refer ANSI/TIA-568.3-D *เป็นขอบเขตของงานติดตั้ง | Digit | dB
| - OFC with pigtails [dB] | ≤0.3dB per point refer ANSI/TIA-568.3-D *เป็นขอบเขตของงานติดตั้ง | Digit | dB
| 13. Number of fibers [cores] | 36 | Digit | core
| 14. Mode field diameter [mm] | 9.2 ± 0.4 µm@ 1310 nm ,10.4 ± 0.5 µm@ 1550 nm | Digit | mm
| 15. Cladding diameter [mm] | 125 ± 0.7µm | Digit | mm
| 16. Mode field concentricity error [mm] | 1µm | Digit | mm
b. | [ ] Multi-mode optical fiber
1 Optical fiber
| 1.1 Type |  | Text
| 1.2 Standard references |  | Text
| 1.3 Maximum attenuation coefficient at 850 nm [dB/km] |  | Digit
| 1.4 Maximum attenuation coefficient at 1,300 nm [dB/km] |  | Digit
2 Indoor-outdoor cables
| 2.1 Maximum tensile load [N] |  | Digit
| 2.2 Bending radius |  | Digit
| 2.3 Number of fibers [cores] |  | Digit
| 2.4 Outer sheath material |  | Text
3.Patch cords
| 3.1 Length [m] |  | Digit
| 3.2 Connector type |  | Text
**Please fill in blue cell

## PD-25 1-1 (FTC-Nov 2024)-1 (hidden)
Proposal Data
PD 25 (1/1)
JOINT BOX, FIBERFRAME TERMINATION FOR LINE TO CUSTOMERS
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | LOCAL
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark
a. | Joint Box
| a1. Capacity conforms to fiber core | [ / ] Yes [ ] No | Yes No
| a2. Max. closure splice capacity [cores] | 96 | Digit
| a3. Max. Number of tray per closure [tray] | 6 (12F) , 4(24F) | Digit
| a4. Splice capacity per tray [cores] | 12&24 | Digit
| a5. Type of Material of closure | PE | Text
| a6. Reinforcement sleeve for each core | [ / ] Yes [ ] No | Yes No
b. | Fiberframe Termination Cabinet
| b1. Capacity conforms to fiber core in | [ / ] Yes [ ] No | Yes No
one subrack
| b2. Max. of Capacity per subrack [cores] | 12 | Digit
| b3. Number of subrack [subrack] | 3 | Digit
| b4. Total of Capacity per [cores] | 36 | Digit
| b5. FC through connector type with | [ / ] Yes [ ] No | Yes No
phosphor bronze sleeve
| b6. Subrack type | [ / ] Sliding drawer
[ ] _ _ _ _ _ _ _ _
| b7. Heat shrink splice protector | [ / ] Yes [ ] No | Yes No
**Please fill in blue cell

## PD-39 1-3 (Relay List-Nov 24)-1 (hidden)
Proposal Data
PD 39 (1/3)
MAIN PROTECTIVE RELAY LIST
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
No. | Specification Detail | Data for 230 kV and below | Data for 500 kV | Format Type ที่ต้องให้ Bidder กรอก | Benmark
A1. | LOW IMPEDANCE BUS DIFFERENTIAL RELAY (PRIMARY)
a. | Manufacturer | TOSHIBA | TOSHIBA | Text
b. | Country of Origin | VIETNAM | VIETNAM | Text
c. | Type | GRB200 | GRB200 | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
e. | Single Phase or Three Phase Relay | 3 Phase | 3 Phase | Text
f | Specify type of configuration | [ / ] Centralized | [ / ] Centralized
| - Maximum feeders per 1 unit | 8 | 8 | Digit
| - Maximum units per 1 system | 1 | 1 | Digit
A2. | LOW IMPEDANCE BUS DIFFERENTIAL RELAY (SECONDARY)
a. | Manufacturer | SIEMENS | SIEMENS | Text
b. | Country of Origin | GERMANY | GERMANY | Text
c. | Type | 7SS85 | 7SS85 | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
e. | Single Phase or Three Phase Relay | 3 Phase | 3 Phase | Text
f. | Specify type of configuration | [ / ] Centralized | [ / ] Centralized
| - Maximum feeders per 1 unit | 8 | 8 | Text
| - Maximum units per 1 system | 1 | 1 | Text
B1. | CURRENT DIFFERENTIAL RELAY (PRIMARY)
a. | Manufacturer | INGETEAM |  | Text
b. | Country of Origin | SPAIN |  | Text
c. | Type | EF-LD |  | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A
e. | Single Phase or Three Phase Relay | 3 Phase |  | Text
f. | Communication Ports
| - Customer's Line : Single Mode (Wavelength : 1310 nm) | [ / ] Yes [ ] No | [ ] Yes [ ] No
| - EGAT's Line : Multimode (Wavelength : 850 nm) | [ / ] Yes [ ] No | [ ] Yes [ ] No
B2. | CURRENT DIFFERENTIAL RELAY (SECONDARY)
a. | Manufacturer |  |  | Text
b. | Country of Origin |  |  | Text
c. | Type |  |  | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A
e. | Single Phase or Three Phase Relay |  |  | Text
f. | Communication Ports
| - Customer's Line : Single Mode (Wavelength : 1310 nm) | [ ] Yes [ ] No | [ ] Yes [ ] No | Yes No
| - EGAT's Line : Multimode (Wavelength : 850 nm) | [ ] Yes [ ] No | [ ] Yes [ ] No | Yes No
C1. | DISTANCE RELAY (PRIMARY)
a. | Manufacturer |  | INGETEAM | Text
b. | Country of Origin |  | SPAIN | Text
c. | Type |  | EF-ZT | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
e. | Single Phase or Three Phase Relay |  | 3 Phase | Text
**Please fill in blue cell

## PD-39 2-3 (Relay List-Nov 24)-1 (hidden)
Proposal Data
PD 39 (2/3)
MAIN PROTECTIVE RELAY LIST
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
No. | Specification Detail | Data for 230 kV and below | Data for 500 kV | Format Type ที่ต้องให้ Bidder กรอก | Benmark
C2. | DISTANCE RELAY (SECONDARY/ BACK UP)
a. | Manufacturer | TOSHIBA | NR ELECTRIC | Text
b. | Country of Origin | VIETNAM | CHINA | Text
c. | Type | GRZ200 | PCS-902 | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
e. | Single Phase or Three Phase Relay | 3 Phase | 3 Phase | Text
D. | DIRECTIONAL OVERCURRENT RELAY
a. | Manufacturer |  |  | Text
b. | Country of Origin |  |  | Text
c. | Type |  |  | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A
E. | OVERCURRENT RELAY
a. | Manufacturer | INGETEAM | INGETEAM | Text
b. | Country of Origin | SPAIN | SPAIN | Text
c. | Type | DA-PT | DA-PT | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
F. | RECLOSING RELAY
a. | Manufacturer | INGETEAM | INGETEAM | Text
b. | Country of Origin | SPAIN | SPAIN | Text
c. | Type | EF-ZT | EF-ZT | Text
d. | Single Phase or Three Phase Relay | 3 Phase | 3 Phase | Text
G. | SYNCHRO-CHECK RELAY (FOR INTERPOSING)
a. | Manufacturer | INGETEAM | INGETEAM | Text
b. | Country of Origin | SPAIN | SPAIN | Text
c. | Type | DA-PT | DA-PT | Text
H. | BREAKER FAILURE RELAY
a. | Manufacturer | INGETEAM | INGETEAM | Text
b. | Country of Origin | SPAIN | SPAIN | Text
c. | Type | EF-ZT | EF-ZT | Text
d. | Current Rating | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
e. | Single Phase or Three Phase Relay | 3 Phase | 3 Phase | Text
f. | End Fault Function | [ / ] Yes [ ] No | [ / ] Yes [ ] No | Yes No
I. | TRANSFORMER DIFFERENTIAL RELAY
a. | Manufacturer |  | TOSHIBA | Text
b. | Country of Origin |  | VIETNAM | Text
c. | Type |  | GRT200 | Text
d. | Number of Windings Application |  | 3 | Digit
e. | Current Rating | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
f. | Single Phase or Three Phase Relay |  | 3 Phase | Text
**Please fill in blue cell

## PD-39 3-3 (Relay List-Nov 24)-1 (hidden)
Proposal Data
PD 39 (3/3)
MAIN PROTECTIVE RELAY LIST
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
No. | Specification Detail | Data for 230 kV and below | Data for 500 kV | Format Type ที่ต้องให้ Bidder กรอก | Benmark
J. | REACTOR DIFFERENTIAL RELAY
a. | Manufacturer |  | SIEMENS | Text
b. | Country of Origin |  | GERMANY | Text
c. | Type |  | 7UT82 | Text
d. | Number of Windings Application |  | 2 | Digit
e. | Current Rating | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A | [ ] 1A only [ ] 5A only [ / ] settable 1 or 5A
f. | Single Phase or Three Phase Relay |  | 3 Phase | Text
K. | C-BANK FEEDER DIFFERENTIAL RELAY
a. | Manufacturer |  |  | Text
b. | Country of Origin |  |  | Text
c. | Type |  |  | Text
d. | Number of Windings Application |  |  | Digit
e. | Current Rating | [ ] 1A only [ ] 5A only [ ] settable 1 or 5A
f. | Single Phase or Three Phase Relay |  |  | Text
L. | UNDERFREQUENCY RELAY
a. | Manufacturer |  |  | Text
b. | Country of Origin |  |  | Text
c. | Type |  |  | Text
M. | UNDERVOLTAGE RELAY
a. | Manufacturer |  |  | Text
b. | Country of Origin |  |  | Text
c. | Type |  |  | Text
N. | OVERVOLTAGE RELAY
a. | Manufacturer |  | INGETEAM | Text
b. | Country of Origin |  | SPAIN | Text
c. | Type |  | DA-PT | Text
O. | UNBALANCE SENSING RELAY
a. | Manufacturer |  |  | Text
b. | Country of Origin |  |  | Text
c. | Type |  |  | Text
P. | OVERFLUXING RELAY
a. | Manufacturer |  |  | Text
b. | Country of Origin |  |  | Text
c. | Type |  |  | Text
**Please fill in blue cell

## 500kV Special Req.TFCT-Nov24-1 (hidden)
Special Requirements for Total Fault Clearing Time without Communication Operating Time for 500 kV Protection System
The total fault clearing time without communication operating time for 500 kV protection system from fault inception to the circuit breaker arc extinction shall comprise of the interrupting time of circuit breaker plus the line protection operating time. The total fault clearing time without communication operating time shall not be more than 70 ms for the line protection which comprises of distance relay and shall not be more than 80 ms for the line protection which comprises of line differential relay. The proposed value of the total fault clearing time without communication operating time shall be specified in the Proposal Data sheet and submitted together with the tender document during the bidding as an evidence for consideration of evaluation. The proposed total time of exceeding the limitation of 70 ms for the line protection which comprises of distance relay and 80 ms for the line protection which comprises of line differential relay is not acceptable and shall constitute sufficient grounds for rejection. The details of the interrupting time shall be as follows:
1. | Interrupting time. The interval between the time when the actuating quantity of the release circuit reaches the operating value, the switching device being in a closed position, and the instant of arc extinction on the primary arcing contacts.(Interrupting time is numerically equal to the sum of opening time and arcing time, In multipole devices, interrupting time may be measured for each pole or for the device as a whole, in which latter case, the interval is measured to the instant of arc extinction in the last pole to clear) The guaranteed interrupting time of circuit breaker shall be verified by the design test record.
2. | Line protection operating time. The maximum time which the main and auxiliary relays use to allow signal for the trip command when any fault with the following characteristics occurs : 2.1 Line protection with distance relay; The fault characteristics : -SIR ≤ 3 -Fault location at 50% of zone 1 setting. -Phase to phase fault (AB, BC, CA, ABC) -Phase to ground fault (AG, BG, CG) The line characteristics : (base MVA=100) -Positive impedance ; R=0.001008 pu., X=0.019117 pu., B=1.852594 pu. -Zero impedance ; R0=0.014532 pu., X0=0.070217 pu., B0=1.268838 pu. -Mutual impedance ; R0=0.013531 pu., X0=0.0511 pu. 2.2 Line protection with line differential relay; The fault characteristics : -When different current is two times of relay setting different current. ( Idiff = 2Idiff-setting) -Phase to phase fault (AB, BC, CA, ABC) -Phase to ground fault (AG, BG, CG)

## Cover FRS - ERL (hidden)
Proposal Data |  | Instruction
Cover page |  | Proposal Data
Bidder name: | IN CONSORTIUM | Name: | Power Circuit Breaker
Bid No: | TIEC-S-06
* If more than one type of equipment is proposed per one proposal data, the bidder shall create additional Excel sheets. For example, if two types of auxiliary relays are used, there must be two PD-16 sheets.
**Please fill in blue cell
ตัวอย่าง
|  | No. | Specification Detail | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark
|  | a. | Make and country of origin
- Circuit breaker
|  |  | - Make | Digit
|  |  | - Country of origin | Digit
- Steel support structure
|  |  | - Make | Digit
|  |  | - Country of origin | Digit
|  | b. | Type
|  |  | - Interupting Medium (SF6, Vacuum, etc) | Digit
|  |  | - Tripping (Three Poles) | YES NO
|  |  | - Tripping (Single pole & Three poles) | YES NO
|  | f. | Rated voltage
|  |  |  | Digit | kV
|  | s. | Control voltage rating
|  |  | - Normal voltage (From) (min) | Digit | Vdc |  | 10
|  |  | - Normal voltage (From) (max) | Digit | Vdc |  | 20
|  |  | - Normal voltage (To) (min) | Digit | Vdc |  | 30
|  |  | - Normal voltage (To) (max) | Digit | Vdc |  | 40
|  |  | - Operation voltage range (min) | Digit | Vdc |  | 100
|  |  | - Operation voltage range (max) | Digit | Vdc |  | 200
|  | A1 | Tower Type:
|  | A1.1 | DAI
|  | A1.1.1 | Basic Body | Text
|  | A1.1.2 | Body Extension | Text
|  | A1.1.3 | Tower Height (m.) | Digit | m. | Ex. 1 -7
กรณีเป็น Row ที่ Bidder กรอก โดยให้สามารถกรอก Format Type เป็น
- Digit
- Text
- Yes No
*หน่วยงานต้องมีการปรับ Template ให้สอดคล้องกับ Template มาตรฐาน
กรณีที่ต้องการเพิ่มคำอธิบายให้ Bidder
(ถ้ามี)
กรอกค่า Benchmark ที่ต้องการให้ระบบทำการเปรียบเทียบ เมื่อมีการเปิดซองและทำการเปรียบเทียบข้อมูลทางเทคนิค
File Format เพื่อนำเข้าสู่ระบบ Excel
กรอกหัวข้อ

## PD-18.2 1-1 (FRS PNL-Nov 20 (2) (hidden)
Proposal Data | [6 empty] | PROPOSAL DATA
PD 18.2 (1/1)
PANEL ASSEMBLY FOR FAULT RECORDING SYSTEM | [6 empty] | PANEL ASSEMBLY FOR FAULT RECORDING SYSTEM
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | PRECISE SYSTEM AND PROJECT CO., LTD. / U-TAH INDUSTRY LTD., PART.
[12 empty] | BIDDER NAME _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | BID NO. _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark | MANUFACTURER_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
a. | Country of Origin | Local(Thailand) | Text |  |  |  | a. | Make and Country of Origin |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
[7 empty] | b. | Engineering Work | (FRS Manufacturer) |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
b. | Engineering Work | ERL (Thailand) Co.,Ltd. | Text |  |  |  | c. | Blank Panel Maker |  |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
[7 empty] | d. | Applied Standards
c. | Blank Panel Maker | PRECISE SYSTEM AND PROJECT CO., LTD./ U-TAH INDUSTRY LTD., PART. | Text | [5 empty] | Dielectric withstand | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
|  | [ / ] I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER). |  |  |  |  | Insulation Resistance | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
d. | Applied Standards | [7 empty] | Temperature Range | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Dielectric withstand | 1500 V | Digit |  |  |  | e. | Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Insulation Resistance | Minimum 0.0092 M-km(cable) | Digit |  |  |  | f. | The thickness of leveled sheet steel and | [ ] Yes | [ ] No
| - Temperature Range [°C] | -10 to 50 | Digit |  |  |  |  | formed steel members is not less than 2.5 mm.
e. | Type | Dual type (Indoor) | Text |  |  |  |  | If no, specify the supporting structure method. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
f. | The thickness of leveled sheet steel and | [ / ] Yes [ ] No | Yes No |  |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| formed steel members is not less than 2.5 mm. | [5 empty] | g. | Degree of protection | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| If no, specify the supporting structure method. |  | Text |  |  |  | h. | Ambient temperature | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ °C
g. | Degree of protection | IP4X | Text |  |  |  | i. | Ambient humidity | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ %
h. | Ambient temperature [°C] | -10 to 55 | Digit | °C |  |  | j. | Terminal Block
i. | Ambient humidity [%] | up to 95% | Digit | % |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
j. | Other equipments [Type / Manufacturer] | [6 empty] | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j1. Test switch | [5 empty] | k. | Miniature Circuit Breaker
| - For Control and Protection | N/A | Text |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Metering | FMS / STATES (FMS-10A for VT, FMS-10F for CT) | Text
| j2. Undervoltage Relay | MY4 / OMRON | Text |  |  |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j3. Terminal Block | [5 empty] | l. | Switchboard wire
| - For AC/DC power supply | UK16N / Phoenix | Text |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For PT and control circuits | USST10 / Phoenix | Text
| - For CT circuits | USST10 / Phoenix | Text |  |  |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Alarm/Status circuits and marshalling cabinet | UK5-MTK-P/P / Phoenix | Text |  |  |  | m. | Test Equipment
| j4. Miniature Circuit Breaker | IC60N / Schneider | Text |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j5. Switchboard wire | Cable Plus PVC, 600V / Cable Plus | Text
[8 empty] | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
k. | Specify type and manufacturer of spectial tool, | N/A | Text |  |  |  | n. | The normal size of drawings. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| if needed. |  | Text |  |  |  |  | If not A1, give reason. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
**Please fill in blue cell

## PD-19 1-2 (FRS-Nov 2024) (2) (hidden)
Proposal Data
PD 19 (1/2)
FAULT RECORDING SYSTEM
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ERLPhase Power Technologies Ltd.
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark
a. | Country of Origin | Canada | Text
b. | Type | TESLA 4000 | Text
c. | Hardware :
| c1. Type and capacity of hard disk | 64 GB Industrial Grade Flash memory | Text
| c2. Easy change every channels between voltage and | [ / ] Yes [ ] No | Yes No
current channels
| If No, give detail |  | Text
| c3. Automatically short CT when remove an analog | [ ] Yes [ / ] No | Yes No
isolator module
| If No, give detail | CT input modules connected test switch to short CT | Text
| c4. Number of bits for A/D converters | 16 bit | Digit
| c5. Have history log or SER log for maintenance | [ / ] Yes [ ] No | Yes No
| c6. Every digital channel shall be start FRS | [ / ] Yes [ ] No | Yes No
independently
| c7. High scan frequency range [Hz] | 1,600 - 19,200 | Digit | Hz
| c8. Slow scan frequency range [Hz] | 50 or 60 | Digit | Hz
| c9. Dual scan frequency | [ / ] Yes [ ] No | Yes No
| c10. Prefault time [ms] | up to 8,000 | Digit | ms
| c11. Postfault time [ms] | up to 30,000 | Digit | ms
| c12. Event time resolution at least 1 ms | [ / ] Yes [ ] No | Yes No
| c13. Total memory > 32 MB for high scan rate | [ / ] Yes [ ] No | Yes No
| c14. Maximum duration per record at 30 Hz scan rate [min] | up to 30 mins of dynamic swing recording at 50 Hz. | Digit | min
| c15. Duration of working (initialization and reset time) | 20 | Digit | sec
inclusion hardware and software [sec]
| c16. User calculate channel shall be save in | [ / ] Yes [ ] No | Yes No
configuration file
| c17. Continuous self diagnostics (watch dog) | [ / ] Yes [ ] No | Yes No
| If No, give detail |  | Text
d. | Software :
| d1. Number of levels to security access (For User) | Up to 32 user defined security level accounts available. 10 default security level accounts provided | Text
Detail
| d2. Open many records simultaneously | [ / ] Yes [ ] No | Yes No
| d3. Each channel are displayed on separate axis | [ / ] Yes [ ] No | Yes No
| d4. All waveforms shall be moved to any position | [ / ] Yes [ ] No | Yes No
| d5. Harmonics order | up to 100th harmonic at 384 samples/cycle | Text
| d6. Backup & restore the record with OS command | [ / ] Yes [ ] No | Yes No
(copy & paste)
| If No, give detail |  | Text
| d7. Standard & version of comtrade file | 1999, ASCII & BINARY | Text
| d8. Every line shall be calculate power flow | [ / ] Yes [ ] No | Yes No
| d9. Have roll back configuration file when is | [ / ] Yes [ ] No | Yes No
communicating (remote failure)
| d10. Have symbolic windows to indicate a status of | [ / ] Yes [ ] No | Yes No
communication that is success or not
| d11. Polling period | From __60 sec_ to _30 min_ | Digit
| d12. Formula for the channel calculate function | 1. 30 Summation channels 2. 12 Sequence channels 3. 18 power channels for calculating Impedance 4. 18 Impedance channels 5. 18 Power factor channels 6. 30 logic channels 7. 12 Frequency channels 8. 10 Fault location channels | Text
| d13. Combining any record in a new file | [ / ] Yes [ ] No | Yes No
| d14. Print chart same on the monitor | [ / ] Yes [ ] No | Yes No
**Please fill in blue cell

## PD-19 2-2 (FRS-Nov 2024) (2) (hidden)
Proposal Data
PD 19 (2/2)
FAULT RECORDING SYSTEM
Bidder name: | IN CONSORTIUM
Bid No: | TIEC-S-06
Manufacturer: | ERLPhase Power Technologies Ltd.
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | หน่วย | วิธีการกรอกข้อมูล | Benmark
e. | Sensor :
e1. Have the starting sensor
| - Overcurrent staring sensor | [ / ] Yes [ ] No | Yes No
| - Undervoltage staring sensor | [ / ] Yes [ ] No | Yes No
| - Frequency staring sensor | [ / ] Yes [ ] No | Yes No
| - Negative sequence voltage starting sensor | [ / ] Yes [ ] No | Yes No
| - Zero sequence voltage starting sensor | [ / ] Yes [ ] No | Yes No
| - Power swing starting sensor | [ / ] Yes [ ] No | Yes No
| - External start | [ / ] Yes [ ] No | Yes No
| e2. Sensor limit operating time [ms] | 1-10,000 | Digit | ms
f. | Front Panel :
| Have a keyboard on front panel to set the FRS | [ ] Yes [ / ] No | Yes No
| If No, give detail | Local HMI is not sufficient for total fault recorder functionally configuration can be done from local PC/Labtop or Central Station PC | Text
g. | Panel Assembly :
| Manufacturer | PRECISE SYSTEM AND PROJECT/U-TAH INDUSTRY | Text
| Country of Origin | LOCAL (THAILAND)
h. | Spare parts :
List of all recommended spare parts :
|  | 1.ANALOG ISOLATOR CARD | Text
|  | 2.POWER SUPPLY | Text
|  | 3.ACQUISITION UNIT | Text
|  | 4.CPU & MEMORY MODULE 1 | Text
|  | 5.ANALOG ISOLATOR FOR VOLTAGE | Text
|  | 6.ANALOG ISOLATOR FOR CURRENT | Text
|  | 7.DIGITAL ISOLATOR MODULE | Text
|  | 8.HARD DISK & HARD DISK CONTROLLER | Text
|  | 9.TELE- COMMUNICATION BOARD | Text
i. | Service
| i1. Startup with manufacturer’s supervisor | [ / ] Yes [ ] No | Yes No
i2. Service maintenance
| - Response time of the after sale service [Days] | 1 | Digit | Days
| - Service respresentative in Thailand | [ / ] Yes [ ] No | Yes No
| i3. 2 years warranty period | [ / ] Yes [ ] No | Yes No
**Please fill in blue cell

## FM-POW-P01 - Precise (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [9 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  |  | PROCUREMENT REFERENCE : |  |  | TIEC-S-06 |  |  |  | Text
48VDC LOAD CENTER |  |  | SCHEDULE NO. |  | 2AB34 |  |  |  |  | Text
|  |  | ITEM NO. | 2AB34-3 | [5 empty] | Text
|  |  | BIDDER : | IN CONSORTIUM | [5 empty] | Text
General Characteristic
a. | Make and Country of Origin |  | Precise Electric Manufacturing Co., Ltd. / Thailand | [6 empty] | Text
b. | Brand/Model |  | Enclosure Type | [6 empty] | Text
c. | Load Center Type |  |  | [X] | Type 1 | [ ] | Type 2 |  |  | Select
d. | Applied Standards |  | IEC | [6 empty] | Text
e. | Applied Charger Capacity for Load Center |  |  | [ ] | 75A | [ ] | 100A | [X] | 150A | Select
|  |  |  | [ ] | 200A | [ ] | 300A | [ ] | Other
f. | Terminal Block
|  | - Brand / Model | PHOENIX / RBO 10 | [6 empty] | Text
|  | - Terminal Block Withstand Current Rating | 309 | [5 empty] | A | Digit
g. | Main Busbar
|  | - Brand / Model | NSC | [6 empty] | Text
|  | - Busbar Current Rating | 465 (1.55A/mm2) | [5 empty] | A | Digit
|  | - Cross-Section Dimension of Busbar | 30 x 10 | [5 empty] | mm x mm | Digit
h. | Rated Voltage 48 V |  |  | [X] | Yes | [ ] | No |  |  | Select
i. | 1-Pole 16A Branch Breaker
|  | - Brand / Model | LS / BK63H | [6 empty] | Text
|  | - Quantity of Breaker | 15 | [5 empty] | EA | Digit
|  | - Trip Rating / Max Voltage | 16 / 250 | [5 empty] | A / V | Digit
|  | - Frame Rating | 63 | [5 empty] | A | Digit
|  | - Interrupting Rating | 10 | [5 empty] | kA | Digit
j. | 1-Pole 32A Branch Breaker
|  | - Brand / Model | LS / BK63H | [6 empty] | Text
|  | - Quantity of Breaker | 30 | [5 empty] | EA | Digit
|  | - Trip Rating / Max Voltage | 32 / 250 | [5 empty] | A / V | Digit
|  | - Frame Rating | 63 | [5 empty] | A | Digit
|  | - Interrupting Rating | 10 | [5 empty] | kA | Digit
k. | 1-Pole 63A Branch Breaker
|  | - Brand / Model | LS / BK63H | [6 empty] | Text
|  | - Quantity of Breaker | 15 | [5 empty] | EA | Digit
|  | - Trip Rating / Max Voltage | 63 / 250 | [5 empty] | A / V | Digit
|  | - Frame Rating | 63 | [5 empty] | A | Digit
|  | - Interrupting Rating | 10 | [5 empty] | kA | Digit
l. | Motor operator
|  | - Brand / Model | SIEMENS / 3VA9257-0HA10 | [6 empty] | Text
|  | - Rated control voltage | 24-60 | [5 empty] | V | Digit
m. | 3-Pole Circuit breaker
|  | - Brand / Model | SIEMENS/3VA12 | [6 empty] | Text
|  | - Rated current | 250/500 | [5 empty] | A / V | Digit
|  | - Frame Rating | 250 | [5 empty] | A | Digit
n. | Voltmeter (0 – 100) V |  |  | [X] | Yes | [ ] | No |  |  | Select
|  | - Brand / Model | ISKRA / BQ0207 | [6 empty] | Text
|  | - Accuracy Class | 1 | [6 empty] | Digit
|  | - Full scale Deflection Angle | 90 | [5 empty] | Degree
Digit
o. | Ammeter (0 – 300) A for load current |  |  | [X] | Yes | [ ] | No |  |  | Select
|  | - Brand / Model | ISKRA / BQ0207 | [6 empty] | Text
|  | - Accuracy Class | 1 | [6 empty] | Digit
|  | - Full scale Deflection Angle | 90 | [5 empty] | Degree | Digit
p. | Ammeter (-300) - (0) – (+300) A for battery charge/ |  |  | [X] | Yes | [ ] | No |  |  | Select
discharge current
|  | - Brand / Model | ISKRA / BQ2207 | [6 empty] | Text
|  | - Accuracy Class | 1 | [6 empty] | Digit
|  | - Full scale Deflection Angle | 240 | [5 empty] | Degree | Digit
q. | Shunt Resistor
|  | - Brand / Model | NOVA / NDS | [6 empty] | Text
|  | - Class | 0.5 | [6 empty] | Digit
|  | - Ratio | 300 / 60 | [5 empty] | A / mV | Digit
r. | Cabinet dimension (WxDxH) |  | W600 x D600 x H2185 | [5 empty] | mm x mm x mm | Digit
s. | Electro Galvanized Sheet Steel Thickness (Cubicle) |  | 1.5 | [5 empty] | mm | Digit
t. | Color RAL 7063 |  |  | [X] | Yes | [ ] | No |  |  | Select
u. | Total Weight |  | 350 | [5 empty] | kg | Digit
v. | Floor Load |  | - | [5 empty] | kg/sq.m | Digit

## FM-POW-P01 - SCI (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [9 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  |  | PROCUREMENT REFERENCE : |  |  | TIEC-S-06 |  |  |  | Text
48VDC LOAD CENTER |  |  | SCHEDULE NO. |  | 2AB34 |  |  |  |  | Text
|  |  | ITEM NO. | 2AB34-3 | [5 empty] | Text
|  |  | BIDDER : | IN CONSORTIUM | [5 empty] | Text
General Characteristic
a. | Make and Country of Origin |  | SCI ELECTRIC PCL / THAILAND | [6 empty] | Text
b. | Brand/Model |  | 2st | [6 empty] | Text
c. | Load Center Type |  |  | [ / ] | Type 1 | [ ] | Type 2 |  |  | Select
d. | Applied Standards | [8 empty] | Text
e. | Applied Charger Capacity for Load Center |  |  | [ ] | 75A | [ ] | 100A | [ / ] | 150A | Select
|  |  |  | [ ] | 200A | [ ] | 300A | [ ] | Other
f. | Terminal Block
|  | - Brand / Model | TOGI/PT-400 | [6 empty] | Text
|  | - Terminal Block Withstand Current Rating | 400 | [5 empty] | A | Digit
g. | Main Busbar
|  | - Brand / Model | ORIENTAL / COPPER BAR | [6 empty] | Text
|  | - Busbar Current Rating | 676 | [5 empty] | A | Digit
|  | - Cross-Section Dimension of Busbar | 40x6 | [5 empty] | mm x mm | Digit
h. | Rated Voltage 48 V |  |  | [ / ] | Yes | [ ] | No |  |  | Select
i. | 1-Pole 16A Branch Breaker
|  | - Brand / Model | ABB/S201M-C | [6 empty] | Text
|  | - Quantity of Breaker | 15 | [5 empty] | EA | Digit
|  | - Trip Rating / Max Voltage | 16/60 | [5 empty] | A / V | Digit
|  | - Frame Rating | 63 | [5 empty] | A | Digit
|  | - Interrupting Rating | 10 | [5 empty] | kA | Digit
j. | 1-Pole 32A Branch Breaker
|  | - Brand / Model | ABB/S201M-C | [6 empty] | Text
|  | - Quantity of Breaker | 30 | [5 empty] | EA | Digit
|  | - Trip Rating / Max Voltage | 32/60 | [5 empty] | A / V | Digit
|  | - Frame Rating | 63 | [5 empty] | A | Digit
|  | - Interrupting Rating | 10 | [5 empty] | kA | Digit
k. | 1-Pole 63A Branch Breaker
|  | - Brand / Model | ABB/S201M-C | [6 empty] | Text
|  | - Quantity of Breaker | 15 | [5 empty] | EA | Digit
|  | - Trip Rating / Max Voltage | 63/60 | [5 empty] | A / V | Digit
|  | - Frame Rating | 63 | [5 empty] | A | Digit
|  | - Interrupting Rating | 10 | [5 empty] | kA | Digit
l. | Motor operator
|  | - Brand / Model | ABB/MOE | [6 empty] | Text
|  | - Rated control voltage | 48-60 ( Min 40.8-Max.66 ) | [5 empty] | V | Digit
m. | 3-Pole Circuit breaker
|  | - Brand / Model | ABB/XT5N400 TMA320 | [6 empty] | Text
|  | - Rated current | 224-320/250 | [5 empty] | A / V | Digit
|  | - Frame Rating | 400 | [5 empty] | A | Digit
n. | Voltmeter (0 – 100) V |  |  | [ / ] | Yes | [ ] | No |  |  | Select
|  | - Brand / Model | APN/DC96-90 | [6 empty] | Text
|  | - Accuracy Class | 1 | [6 empty] | Digit
|  | - Full scale Deflection Angle | 90 | [5 empty] | Degree
Digit
o. | Ammeter (0 – 300) A for load current |  |  | [ / ] | Yes | [ ] | No |  |  | Select
|  | - Brand / Model | APN/DC96-240 | [6 empty] | Text
|  | - Accuracy Class | 1 | [6 empty] | Digit
|  | - Full scale Deflection Angle | 240 | [5 empty] | Degree | Digit
p. | Ammeter (-300) - (0) – (+300) A for battery charge/ |  |  | [ / ] | Yes | [ ] | No |  |  | Select
discharge current
|  | - Brand / Model | APN/DC96-240 | [6 empty] | Text
|  | - Accuracy Class | 1 | [6 empty] | Digit
|  | - Full scale Deflection Angle | 240 | [5 empty] | Degree | Digit
q. | Shunt Resistor
|  | - Brand / Model | APN/SHUNT 300A/60mV | [6 empty] | Text
|  | - Class | 1 | [6 empty] | Digit
|  | - Ratio | 300/60 | [5 empty] | A / mV | Digit
r. | Cabinet dimension (WxDxH) |  | 600x600x2185 | [5 empty] | mm x mm x mm | Digit
s. | Electro Galvanized Sheet Steel Thickness (Cubicle) |  | 1.6 | [5 empty] | mm | Digit
t. | Color RAL 7063 |  |  | [ / ] | Yes | [ ] | No |  |  | Select
u. | Total Weight |  | Approx.650 | [5 empty] | kg | Digit
v. | Floor Load | [7 empty] | kg/sq.m | Digit

## FM-POW-P02 - Hoppecke (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [8 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  | PROCUREMENT REFERENCE : |  |  | TIEC-S-06 |  |  |  | Text
48 VDC VENTED STATIONARY LEAD-ACID BATTERY |  | SCHEDULE NO. |  |  | 2AB34 |  |  |  | Text
|  | ITEM NO. |  | 2AB34 |  |  |  |  | Text
|  | BIDDER : |  | IN CONSORTIUM |  |  |  |  | Text
1. | Make and Country of Origin | HOPPECKE / Germany | [6 empty] | Text
2. | Brand/Model | 6 OPzS 600 | [6 empty] | Text
3. | Capacity at 10 hr. rated 1.80 VPC. 25o C | 686 |  |  |  |  | Ah |  | Digit
4. | Type
| - Vented Stationary Lead-Acid type |  | [ x ] | Yes | [ ] | No |  |  | Yes No
5. | Codes and standards | IEC 60896-1/DIN40736-1 | [6 empty] | Text
6. | Battery Configuration
| - Number of cell per set | 24 |  |  |  |  | Cell |  | Digit
Technical requirement for Battery (24 cells)
1. | Nominal voltage | 48 |  |  |  |  | V |  | Digit
2. | Current capacity | 686 |  |  |  |  | Ah |  | Digit
3. | Discharge characteristic | 43.2V of final voltage based on a |  |  |  | 10 | hour discharge rate |  | Digit
4. | Battery life at 20 Co | 20 |  |  |  |  | Years |  | Digit
5. | Manufacturing age | No longer than |  | 3 | months since the manufacturing date |  |  |  | Digit
6. | Temperature | 5-40 |  |  |  |  | Co |  | Digit
7. | Relative humidity | 30-95 |  |  |  |  | % |  | Digit
8. | Self-discharge rate (per month) | <3 |  |  |  |  | % |  | Digit
Technical requirement for Cell
1. | Volt per cell | 2 |  |  |  |  | V |  | Digit
2. | Discharge characteristic | Final voltage of 1.8 V based on an |  |  |  | 10 | hours discharge rate |  | Digit
3. | Component
| - Positive plate shall be Tubular type |  | [ x ] | Yes | [ ] | No |  |  | Yes No
| - Negative plate shall be Pasted/Flat type |  | [ x ] | Yes | [ ] | No |  |  | Yes No
| - Lead antimony plate |  | [ x ] | Yes | [ ] | No |  |  | Yes No
4. | Container and cover
| - The container shall be made of transparent SAN and cover |  | [ x ] | Yes | [ ] | No |  |  | Yes No
of each cell shall be made of ABS.
| - Container and cover shall have inherent acid-resisting, |  | [ x ] | Yes | [ ] | No |  |  | Yes No
shock-absorbing, heat-resisting , acid leak-proof qualification.
5. | Electrolyte
| - A dilute translucent sulfuric acid shall be used as an electrolyte. |  | [ x ] | Yes | [ ] | No |  |  | Yes No
The substance shall conform to the ITSI standard and it shall be
free from organic, iron, platinum and other impurities that may be
harmful to the battery life.
| - The specific gravity | 1.24 kg / L
| - 10% of the total volume of tropical electrolyte provided in |  | [ x ] | Yes | [ ] | No |  |  | Yes No
the contract shall be spared as an extra and it shall, as well,
conform to the ITSI standard.
| - The containers of electrolyte provided for EGAT shall be newly |  | [ x ] | Yes | [ ] | No |  |  | Yes No
made and they shall conform to the ITSI standard.
6. | Connector
| - Shall be flexible lead or copper material with insulation sheath covered. |  | [ x ] | Yes | [ ] | No |  |  | Yes No
7. | Bolts, nuts and washers
| - Made of metal with acid-resisting and rust-free qualification. |  | [ x ] | Yes | [ ] | No |  |  | Yes No
8. | Bus cover and terminal
| - Shall be electrical insulator. |  | [ x ] | Yes | [ ] | No |  |  | Yes No
9. | Cell numbering label
| - The running cell numbering label shall be specified |  | [ x ] | Yes | [ ] | No |  |  | Yes No
in sequence, i.e. 1, 2, 3 … 24.
10. | Spare accessories
Shall be required to supply extra accessories as follows
| - 4 sets of inter-cell connector and 1 set of inter-step connector |  | [ x ] | Yes | [ ] | No |  |  | Yes No
| - 2 sets of bolts, nuts and washers |  | [ x ] | Yes | [ ] | No |  |  | Yes No
| - 2 sets of bus cover and terminal. |  | [ x ] | Yes | [ ] | No |  |  | Yes No
Technical requirement for battery rack
1. | Rack structure
| - Shall be made of steel material with 2-step structure. |  | [ x ] | Yes | [ ] | No |  |  | Yes No
| - The rail of each row shall be covered with hard rubber |  | [ x ] | Yes | [ ] | No |  |  | Yes No
sheet in order to prevent any damages on the battery cell.
2. | Color
| - Shall be painted with acid resistant gray color RAL7036 |  | [ x ] | Yes | [ ] | No |  |  | Yes No
with double coating procedure.
Accessories and maintenance tools
1. | Rod type thermometer | 3 |  |  |  |  | sets |  | Digit
2. | Syringe type hydrometer | 3 |  |  |  |  | sets |  | Digit
3. | Acid jug | 1 |  |  |  |  | each |  | Digit
4. | Filling funnel | 1 |  |  |  |  | each |  | Digit
5. | Non-oxide grease | 1 |  |  |  |  | can |  | Digit
6. | Filling syringe | 1 |  |  |  |  | each |  | Digit
7. | Acid-resistance glove | 2 |  |  |  |  | pairs |  | Digit
8. | Installation, Operation and Maintenance Manual | 1 |  |  |  |  | set |  | Digit
9. | AC/DC Clamp Meter | 1 |  |  |  |  | set |  | Digit
10. | Maintenance tool box to accommodate the above accessories | 2 |  |  |  |  | boxes |  | Digit
Other
1. | Float charging voltage applied per cell | 2.23 +/-1% |  |  |  |  | V |  | Digit
2. | Equalize charging voltage applied per cell | 2.33 - 2.40 |  |  |  |  | V |  | Digit
3. | Battery cells :
| - Dimension | 147x208x710 |  |  |  |  | (LxWxH) | mm | Digit
| - Weight | 46.1 |  |  |  |  | kg |  | Digit
4. | Battery rack :
| - Dimension | 2000x580x800 |  |  |  |  | (LxWxH) | mm | Digit
| - Weight | 60 |  |  |  |  | kg |  | Digit
| - Arrangement of modules equipped in a rack |  | 1 | Row | 2 | Tier |  |  | Digit
| - Floor loading | 960 |  |  |  |  | kg/sq.mm |  | Digit

## FM-POW-P03 - Exzon (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [8 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  | PROCUREMENT REFERENCE : |  |  |  | TIEC-S-06 |  |  | Text
48VDC CONVENTIONAL TYPE CHARGER |  | SCHEDULE NO. |  |  |  | 2AB34 |  |  | Text
|  | ITEM NO. |  |  | 2AB34 |  |  |  | Text
|  | BIDDER : |  |  | IN CONSORTIUM |  |  |  | Text
a. | Make and Country of Origin |  | THAILAND | [5 empty] | Text
b. | Brand/Model |  | EXZON / LFB3-048-150 | [5 empty] | Text
c. | Type |  | [ x ] | Constant voltage, Silicon control rectifier, |  |  |  |  | Select
Current limit type with isolate transfomer
|  |  | [ ] | Other |  |  |  |  | Text
d. | Applied standard |  | NEMA-PE5 , DIN41773 | [5 empty] | Text
e. | AC input
| - No. of phase |  | 3 Phase , 3 Wire |  |  |  |  | Phase | Digit
| - Voltage range (line to line) |  | 380 +/- 10% |  |  |  |  | V | Digit
| - Maximum current per phase |  | 28 |  |  |  |  | A | Digit
| - frequency range |  | 47.5 - 52.5 |  |  |  |  | Hz | Digit
| - Protection |  | [ x ] | Transient voltage protection, The maximum |  |  |  |  | Select
current @ 8/20 µs not less than 15 kA.(MOV)
|  |  | [ x ] | Circuit breaker with thermal magnetic trip |  |  |  |  | Select
|  |  | [ x] | Other | Ground bus for grounding system |  |  |  | Text
f. | DC output
| - Rate current |  | 150 |  |  |  |  | A | Digit
| - Protection |  | [ x ] | Transient voltage protection, The maximum |  |  |  |  | Select
current @ 8/20 µs not less than 15 kA.(MOV)
|  |  | [ x ] | Circuit breaker with thermal magnetic trip |  |  |  |  | Select
|  |  | [ x ] | Current limited at 110% of rated output current |  |  |  |  | Select
|  |  | [ ] | Other |  |  |  |  | Text
| - DC output voltage |  | 48 |  |  |  |  | V | Digit
| - Ripple voltage output |  | Not exceed 1 |  |  |  |  | % | Digit
| - Voltage regulation |  | +/-1 |  |  |  |  | % | Digit
g. | Efficiency at full load |  | ≥85 |  |  |  |  | % | Digit
h. | Powerf factor at fulload |  | ≥80 |  |  |  |  | % | Digit
i. | Cooling method |  | [ ] | Fan |  | [ x ] | Natural |  | Select
j. | Ambient temperature |  | 0 - 40 |  |  |  |  | Co | Digit
k. | Relative humidity |  | 95 |  |  |  |  | % | Digit
l. | Allowable mimimum battery voltage before charge |  | 30 |  |  |  |  | V | Digit
m. | Float voltage adjustment range |  | 40 to 65 |  |  |  |  | V | Digit
n. | Equalizing voltage adjustment range |  | 40 to 65 |  |  |  |  | V | Digit
o. | Parallel operation permission |  | [ x ] | Yes |  | [ ] | No |  | Yes No
p. | DC output metering |  | [ x ] | Digital |  | [ ] | Analog |  | Select
| - Class |  | 0.5 | [5 empty] | Digit
q. | Alarm function |  | [ x ] | Loss of AC input alarm |  |  |  |  | Select
|  |  | [ x ] | Charge fail alarm |  |  |  |  | Select
|  |  | [ x ] | Low voltage alarm |  | 40-48 |  | V | Select and Digit
|  |  | [ x ] | High voltage alarm |  | 57-59 |  | V | Select and Digit
|  |  | [ x ] | Low Battery alarm |  | 40-48 |  | V | Select and Digit
|  |  | [ x ] | Common alarm |  |  |  |  | Select
|  |  | [ ] | Other |  |  |  |  | Text
r. | Management |  | [ x ] | Float-Equalize charge. |  |  |  |  | Select
|  |  | [ ] | Other |  |  |  |  | Text
s. | Monitoring point |  | [ x ] | Alarm |  |  |  |  | Select
|  |  | [ x ] | Charge mode |  |  |  |  | Select
|  |  | [ x ] | Current and Voltage from charge's front panel. |  |  |  |  | Select
|  |  | [ x ] | Other | Ethernet interface |  |  |  | Text
t. | Storage |  | >400 |  |  |  |  | event | Digit
u. | Dimension
| - Length |  | 600 |  |  |  |  | mm | Digit
| - Width |  | 600 |  |  |  |  | mm | Digit
| - Height |  | 1800 |  |  |  |  | mm | Digit
v. | Weight |  | 340 |  |  |  |  | kg | Digit
w. | Floor loading |  | 950 |  |  |  |  | kg/sq m | Digit
x. | Ingress protection (IP) Class |  | IP21 | [5 empty] | Digit

## FM-FOT-P13 - HBC (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [7 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  |  | PROCUREMENT REFERENCE : |  |  | TIEC-S-06 |  | Text
OPTICAL FIBER CABLE (OFC) |  |  | SCHEDULE NO. |  | 2AB35, 3AB35, 4AB35 |  |  | Text
|  |  | ITEM NO. | 2AB35-1.1,2AB35-2.1,2AB35-3.1,3AB35-1.1,4AB35-1.1 |  |  |  | Text
|  |  | BIDDER : | IN CONSORTIUM |  |  |  | Text
1. | Make and country of origin |  | Thailand |  |  |  |  | Text
2. | Brand/Model |  | HBC / OFC Double Jacket 36C |  |  |  |  | Text
3. | OFC Type |  | [ / ] | Single Sheath Non-metallic |  |  |  | Select
|  |  | [ ] | Double Sheath Non-metallic |  |  |  | Select
4. | ITU-T Recommendation |  | [ / ] | G.652D |  | [ ] | G.652C | Select
5. | Optical fiber characteristics
| - Profile of optical fiber |  | [ / ] | Single mode stepped index |  |  |  | Select
| - Number of optical fibers |  | 36 |  |  |  | core | Digit
| - Mode field diameter @ 1310 nm |  | 9 ± 1.0 |  |  |  | µm | Digit
| - Cladding diameter |  | 125 ± 1 |  |  |  | µm | Digit
| - Mode field concentricity error |  | Max. 1.0 |  |  |  | µm | Digit
| - Cladding noncircularity |  | Less than 2 |  |  |  | % | Digit
| - Cable cut-off wavelength |  | Less than 1260 |  |  |  | nm | Digit
| - Proof stress |  | 0.69 |  |  |  | GPa | Digit
- Chromatic dispersion coefficient
|  | @ wavelength 1310 nm | Less than 3.5 |  |  |  | ps/(nm·km) | Digit
|  | @ wavelength 1550 nm | Less than 20 |  |  |  | ps/(nm·km) | Digit
- Attenuation coefficient
|  | @ wavelength 1310 nm | Max. 0.35 |  |  |  | dB/km | Digit
|  | @ wavelength 1550 nm | Max. 0.21 |  |  |  | dB/km | Digit
| - Polarization mode dispersion coefficient |  | Less than 0.2 |  |  |  | ps/√km | Digit
| - Normal operating temperature |  | -10 to 70 |  |  |  | °C | Digit
7. | Mechanical properties
| - Allowable tension |  | 120 |  |  |  | kg | Digit
| - Bending radius |  | 222 |  |  |  | mm | Digit
| - Overall Diameter |  | 11.1 |  |  |  | mm | Digit
| - Weight |  | 87 |  |  |  | kg/km | Digit
| - Splice loss |  | [ / ] | shall not be more than 0.07 dB |  |  |  | Select

## FM-FOT-P15-Fiberframe PSP (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [7 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  |  | PROCUREMENT REFERENCE : |  |  | TIEC-S-06 |  | Text
JOINT BOX, FIBERFRAME TERMINATON CABINET , INSULATOR |  |  | SCHEDULE NO. |  | 2AB35, 3AB35, 4AB35 |  |  | Text
|  |  | ITEM NO. | 2AB35-1.1, 2AB35-2.1, 2AB35-3.1, 3AB35-1.1, 4AB35-1.1 |  |  |  | Text
|  |  | BIDDER : | IN CONSORTIUM |  |  |  | Text
Joint Box
| Item No. | [6 empty] | Text
| Brand/Model | [6 empty] | Text
| Make and country of origin | [6 empty] | Text
| Capacity conform to fiber core |  | [ ] | confirm |  | [ ] | not confirm | Select
| Max closure splice capacity | [5 empty] | cores | Digit
| Max number of tray per closure | [5 empty] | tray | Digit
| Splice capacity per tray | [5 empty] | cores | Digit
| Type of Material of closure | [6 empty] | Text
| Reinforcement sleeve for each core |  | [ ] | confirm |  | [ ] | not confirm | Select
Fiberframe Termination Cabinet
| Item No. |  | 2AB35-1.1,2AB35-2.1,2AB35-3.1,3AB35-1.1,4AB35-1.1 |  |  |  |  | Text
| Make and country of origin |  | Thailand |  |  |  |  | Text
| Brand/Model |  | PSP |  |  |  |  | Text
| Capacity conform to fiber core in one subrack |  | [ / ] | confirm |  | [ ] | not confirm | Select
| Number of subrack |  | 1 |  |  |  | subrack | Digit
| Max of capacity per subrack |  | 36 |  |  |  | cores | Digit
| Total of capacity |  | 36 |  |  |  | cores | Digit
FC Through connector type with
| phospher bronze sleeve |  | [ / ] | confirm |  | [ ] | not confirm | Select
| Subrack type : | Sliding drawer | [ / ] | confirm |  | [ ] | not confirm | Select
| Heat shrink splice protector |  | [ / ] | confirm |  | [ ] | not confirm | Select
Insulator
| Item No. | [6 empty] | Text
| Brand/Model | [6 empty] | Text
| Make and Country of origin | [6 empty] | Text
| Catalogue supplied |  | [ ] | confirm |  | [ ] | not confirm | Select

## FM-FOT-P15-Fiberframe Gateway (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [7 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  |  | PROCUREMENT REFERENCE : |  |  | TIEC-S-06 |  | Text
JOINT BOX, FIBERFRAME TERMINATON CABINET , INSULATOR |  |  | SCHEDULE NO. |  | 2AB35, 3AB35, 4AB35 |  |  | Text
|  |  | ITEM NO. | 2AB35-1.1, 2AB35-2.1, 2AB35-3.1, 3AB35-1.1, 4AB35-1.1 |  |  |  | Text
|  |  | BIDDER : | IN CONSORTIUM |  |  |  | Text
Joint Box
| Item No. | [6 empty] | Text
| Brand/Model | [6 empty] | Text
| Make and country of origin | [6 empty] | Text
| Capacity conform to fiber core |  | [ ] | confirm |  | [ ] | not confirm | Select
| Max closure splice capacity | [5 empty] | cores | Digit
| Max number of tray per closure | [5 empty] | tray | Digit
| Splice capacity per tray | [5 empty] | cores | Digit
| Type of Material of closure | [6 empty] | Text
| Reinforcement sleeve for each core |  | [ ] | confirm |  | [ ] | not confirm | Select
Fiberframe Termination Cabinet
| Item No. |  | 1AB35-1.1(e),1AB35-2.1(d),1AB35-3.1(d) |  |  |  |  | Text
| Make and country of origin |  | THAILAND |  |  |  |  | Text
| Brand/Model |  | Gateway Plus/GP-48SEGAT |  |  |  |  | Text
| Capacity conform to fiber core in one subrack |  | [ / ] | confirm |  | [ ] | not confirm | Select
| Number of subrack |  | 3 |  |  |  | subrack | Digit
| Max of capacity per subrack |  | 12 |  |  |  | cores | Digit
| Total of capacity |  | 36 |  |  |  | cores | Digit
FC Through connector type with
| phospher bronze sleeve |  | [ / ] | confirm |  | [ ] | not confirm | Select
| Subrack type : | Sliding drawer | [ / ] | confirm |  | [ ] | not confirm | Select
| Heat shrink splice protector |  | [ / ] | confirm |  | [ ] | not confirm | Select
Insulator
| Item No. | [6 empty] | Text
| Brand/Model | [6 empty] | Text
| Make and Country of origin | [6 empty] | Text
| Catalogue supplied |  | [ ] | confirm |  | [ ] | not confirm | Select

## AB12_Power Box - Precise (1) (hidden)
POWER BOX
FORM PD POWER BOX
Mar. 2026
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-10
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 25x10 |  |  |  | mm*mm
| - Branch Bus |  |  | 12x3 |  |  |  | mm*mm
| - Ground Bus |  |  | 25x10 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 380 |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN101d
| - Trip Rating/Max Voltage |  |  | 60 / 690 |  |  |  | A/V
| - Frame Rating |  |  | 100 |  |  |  | A
| - Interrupting Rating |  |  | 25 |  |  |  | kA
g. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN103c
| - Trip Rating/Max Voltage |  |  | 30 / 690 |  |  |  | A/V
| - Frame Rating |  |  | 125 |  |  |  | A
| - Interrupting Rating |  |  | 37 |  |  |  | kA
h. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / ABN203c
| - Trip Rating/Max Voltage |  |  | 200 / 690 |  |  |  | A/V
| - Frame Rating |  |  | 250 |  |  |  | A
| - Interrupting Rating |  |  | 37 |  |  |  | kA
i. | Lighting Relay
| - Make/Type |  |  | MITSUBISHI / S-T25
| - Rated Coil Current/Voltage |  |  | 0.024 / 220 |  |  |  | A/V
| - Contact Current/Voltage Capacity |  |  | 30 / 380 |  |  |  | A/V
j. | Time Switch
| - Make/Type |  |  | PANASONIC / TB38N
| - Rated Current/Voltage |  |  | 20A/240V(Contact), 0.0083/240V(Coil) |  |  |  | A/V
| - Continuous operation in case of power failure |  |  | 300 |  |  |  | Hours
| - Contact Current Capacity |  |  | 20 |  |  |  | A
k. | Changeover Switch
| - Make/Type |  |  | K&N / CA10
| - Rated Current/Voltage |  |  | 20 / 600 |  |  |  | A/V
l. | Power Box Dimensions
| - PRB-1 |  |  | H1050 x W(800+50(L)+50(R)) x D(250+60(F)) |  |  |  | mm×mm×mm
| - PRB-2 & PRB-3 | [6 empty] | mm×mm×mm
m. | Sheet Steel Thickness
| - PRB-1 |  |  | 2.5 |  |  |  | mm
| - PRB-2 & PRB-3 | [6 empty] | mm
n. | Total Weight
| - PRB-1 |  |  | 150 |  |  |  | kg
| - PRB-2 & PRB-3 | [6 empty] | kg

## AB12_Power Box - Precise (2) (hidden)
POWER BOX
FORM PD POWER BOX
Mar. 2026
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-11
a. | Make and Country of Origin |  |  | Precise Electric Manufacturing Co., Ltd. / Thailand
b. | Type / Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 15x3 |  |  |  | mm*mm
| - Branch Bus |  |  | 15x3 |  |  |  | mm*mm
| - Ground Bus |  |  | 15x3 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 380 |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN101d
| - Trip Rating/Max Voltage |  |  | 15, 30 / 690 |  |  |  | A/V
| - Frame Rating |  |  | 100 |  |  |  | A
| - Interrupting Rating |  |  | 25 |  |  |  | kA
g. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / |  |  |  | A/V
| - Frame Rating | [6 empty] | A
| - Interrupting Rating | [6 empty] | kA
h. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / |  |  |  | A/V
| - Frame Rating | [6 empty] | A
| - Interrupting Rating | [6 empty] | kA
i. | Lighting Relay
| - Make/Type |  |  | /
| - Rated Coil Current/Voltage |  |  | / |  |  |  | A/V
| - Contact Current/Voltage Capacity |  |  | / |  |  |  | A/V
j. | Time Switch
- Make/Type
| - Rated Current/Voltage | [6 empty] | A/V
| - Continuous operation in case of power failure | [6 empty] | Hours
| - Contact Current Capacity | [6 empty] | A
k. | Changeover Switch
| - Make/Type |  |  | /
| - Rated Current/Voltage | [6 empty] | A/V
l. | Power Box Dimensions
| - PRB-1 |  |  | H300 x W(200+50(L)+50(R)) x D(120+60(F)) |  |  |  | mm×mm×mm
| - PRB-2 & PRB-3 | [6 empty] | mm×mm×mm
m. | Sheet Steel Thickness
| - PRB-1 |  |  | 2.5 |  |  |  | mm
| - PRB-2 & PRB-3 | [6 empty] | mm
n. | Total Weight
| - PRB-1 |  |  | 75 |  |  |  | kg
| - PRB-2 & PRB-3 | [6 empty] | kg

## AB12_Power Box - SCI (1) (hidden)
POWER BOX
FORM PD POWER BOX
Mar. 2026
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-10
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type / Model No |  |  | 2wm ( Outdoor Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 20x3 |  |  |  | mm*mm
| - Branch Bus |  |  | 12x3 |  |  |  | mm*mm
| - Ground Bus |  |  | 20x3 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 380/220 |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1C125
| - Trip Rating/Max Voltage |  |  | 30/415 |  |  |  | A/V
| - Frame Rating |  |  | 125 |  |  |  | A
| - Interrupting Rating |  |  | 18 @ 240VAC |  |  |  | kA
g. | 3-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1A125
| - Trip Rating/Max Voltage |  |  | 30, 50/550 |  |  |  | A/V
| - Frame Rating |  |  | 125 |  |  |  | A
| - Interrupting Rating |  |  | 10 @ 415VAC |  |  |  | kA
h. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/A2B250
| - Trip Rating/Max Voltage |  |  | 200/550 |  |  |  | A/V
| - Frame Rating |  |  | 250 |  |  |  | A
| - Interrupting Rating |  |  | 18 @ 415VAC |  |  |  | kA
i. | Lighting Relay
| - Make/Type |  |  | ABB /AF16-30
| - Rated Coil Current/Voltage |  |  | 0.0096 / 100-250 |  |  |  | A/V
| - Contact Current/Voltage Capacity |  |  | 30 / 690 |  |  |  | A/V
j. | Time Switch
| - Make/Type |  |  | MULLER / SC 18.10 EASY
| - Rated Current/Voltage |  |  | 0.00435 /230 |  |  |  | A/V
| - Continuous operation in case of power failure |  |  | 10 Years battery-reserve |  |  |  | Hours
| - Contact Current Capacity |  |  | 16 |  |  |  | A
k. | Changeover Switch
| - Make/Type |  |  | NOVA / NCS-20M2
| - Rated Current/Voltage |  |  | 20 /690 |  |  |  | A/V
l. | Power Box Dimensions
| - PRB-1 |  |  | 700Wx950Hx250D |  |  |  | mm×mm×mm
| - PRB-2 & PRB-3 | [6 empty] | mm×mm×mm
m. | Sheet Steel Thickness
| - PRB-1 |  |  | 3 |  |  |  | mm
| - PRB-2 & PRB-3 | [6 empty] | mm
n. | Total Weight
| - PRB-1 |  |  | Approx. 65 |  |  |  | kg
| - PRB-2 & PRB-3 | [6 empty] | kg

## AB12_Power Box - SCI (2) (hidden)
POWER BOX
FORM PD POWER BOX
Mar. 2026
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | TIEC-S-06 | SCHEDULE NO. |  | 1AB12
BIDDER |  | IN CONSORTIUM |  | ITEM NO. | 1AB12-11
a. | Make and Country of Origin |  |  | SCI Electric PCL/Thailand
b. | Type / Model No |  |  | 2wm ( Outdoor Metal enclosed )
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 12x3 |  |  |  | mm*mm
| - Branch Bus | [6 empty] | mm*mm
| - Ground Bus |  |  | 12x3 |  |  |  | mm*mm
e. | Rated Voltage |  |  | 380/220 |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | ABB/A1C125
| - Trip Rating/Max Voltage |  |  | 15, 30/415 |  |  |  | A/V
| - Frame Rating |  |  | 125 |  |  |  | A
| - Interrupting Rating |  |  | 18 @ 240VAC |  |  |  | kA
g. | 3-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / |  |  |  | A/V
| - Frame Rating | [6 empty] | A
| - Interrupting Rating | [6 empty] | kA
h. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / |  |  |  | A/V
| - Frame Rating | [6 empty] | A
| - Interrupting Rating | [6 empty] | kA
i. | Lighting Relay
| - Make/Type |  |  | /
| - Rated Coil Current/Voltage |  |  | / |  |  |  | A/V
| - Contact Current/Voltage Capacity |  |  | / |  |  |  | A/V
j. | Time Switch
| - Make/Type |  |  | /
| - Rated Current/Voltage |  |  | / |  |  |  | A/V
| - Continuous operation in case of power failure | [6 empty] | Hours
| - Contact Current Capacity | [6 empty] | A
k. | Changeover Switch
| - Make/Type |  |  | /
| - Rated Current/Voltage |  |  | / |  |  |  | A/V
l. | Power Box Dimensions
| - PRB-1 | [6 empty] | mm×mm×mm
| - PRB-2 & PRB-3 |  |  | 250Wx300Hx150D |  |  |  | mm×mm×mm
m. | Sheet Steel Thickness
| - PRB-1 |  |  | 2 |  |  |  | mm
| - PRB-2 & PRB-3 | [6 empty] | mm
n. | Total Weight
| - PRB-1 | [6 empty] | kg
| - PRB-2 & PRB-3 |  |  | Approx. 20 |  |  |  | kg