## cleat1
CABLE CLEATS
PD 326.CC
Dec.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | CONSORTIUM OF SCI ELECTRIC PUBLIC COMPANY LIMITED AND NARI GROUP CORPORATION /Thailand-P.R China |  | ITEM NO. |  | 1AB16-2
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  | CMP PRODUCTS
|  | - Country of origin |  | UNITED KINGDOM
b. | Type/Model[1] |  |  | PATRIOT-HT (SDSS) SDSS030035HT
c. | For XLPE Cable Suitability[1]
| - Overall Diameter Range |  |  | Min | 30 | mm. |  | Max | 35 | mm.
d. | Applied Standard |  |  | conforming with EGAT requirement (IEC 61914)
*in case of other, please specify in the box below:
e. | Classification according to material[2] |  |  |  | Metallic
Material :
|  |  |  | X | Composite
[5 empty] | Material : | 316L Stainless Steel
[5 empty] | and | with Standard Polymer Liner Standard Polymer Liners are classified as Low Smoke and Fume Zero Halogen (LSF0H), Phosphorus-free
f. | Resistant to electromechanical forces, withstanding more than one short circuit[3]
| - Cable centre spacing (S) |  |  | 36 |  | mm
| - The peak short circuit current of the 2nd shortcircuit |  |  | 108 |  | kA
| - Lineal spacing (D) |  |  | 600 |  | mm
g. | Formation |  |  | Trefoil
| Note [1]: | The exact size of Cable Cleat shall be confirmed after the exact overall diameter of XLPE power cable is confirmed during project stage.
| Note [2]: | Definitions comply with IEC 61914. metallic consisting of metal only. composite consisting of metallic and non-metallic materials.
a) Fibre reinforced resin materials are not considered to be composite.
b) Materials include any materials supplied by the manufacturer as part of a cable cleat or intermediate restraint or with a cable cleat or intermediate restraint in the same packaging. This may include fixings such as nuts, bolts, screws, washers, springs and pins.
| Note [3]: | The data specified in this item shall conform to the Type Test Report of the type proposed.
| Note [4]: | The values shall be based on the same cables and conditions of the test for resistance to electromechanical forces specified in IEC 61914.