## cleat
CABLE CLEATS
PD 326.CC
[10 empty] | Dec.2024 | [5 empty] | รายการตรวจ Cable cleat
PROPOSAL DATA | [11 empty] | comment |  |  | 1 | Material
PROCUREMENT REFERENCE |  |  | RTS3-S-02 |  | SCHEDULE NO. |  |  | 1AB16 |  |  |  | waiting for discussion with P'Ja |  |  |  | 1.1 | Metallic: | ALUMINUM 5000 SERIES
BIDDER |  | Precise System and Project Co., Ltd. |  |  | ITEM NO. |  | 1AB16-2 | [10 empty] | SS316L Stainless steel
[16 empty] | 1.2 | Composite:
[18 empty] | Metalic part | ALUMINUM 5000 SERIES
SS316L Stainless steel
a. | Manufacturer and Country of Origin | [16 empty] | non-metallic part | ANY
|  | - Manufacturer |  |  | NORMA GROUP
|  | - Country of origin |  |  | CHINA | [9 empty] | 2 | Force/1Cleat must be more than RF EGAT
[12 empty] | ปรับให้พิจารณาแค่ type โดยขนาดของ cleat |  |  |  | 2.1 | FLAT
b. | Type/Model[1] |  |  |  | FF-T2935 | [6 empty] | จะพิจารณาในขั้นบริหารสัญญา | [5 empty] | Calculated result | #REF!
c. | For XLPE Cable Suitability[1] | [10 empty] | ตัดออกเนื่องจากพิจารณาขนาด
| - Overall Diameter Range |  |  |  | Min | 29 | mm. |  | Max | 35 | mm. | ในขั้นบริหารสัญญา
d. | Applied Standard |  |  |  | conforming with EGAT requirement (IEC 61914)
*in case of other, please specify in the box below:
e. | Classification according to material[2] |  |  |  |  | Metallic | [5 empty] | แก้รูปแบบ
Material :
[5 empty] | X | Composite
[6 empty] | Material : | Stainless Steel | [9 empty] | EGAT
[6 empty] | and | Polyolefin | [9 empty] | V | I short circuit | Lineal Spacing | FLAT Force | TREFOIL Force
f. | Resistant to electromechanical forces, withstanding more than one short circuit[3] | [15 empty] | 230 | 170 |  | #REF! | #REF!
| - Cable centre spacing (S) |  |  |  | 35 |  | mm |  |  |  |  | 0.16 | 0.17 | #REF! |  |  |  | Force
| - The peak short circuit current of the 2nd shortcircuit |  |  |  | 125 |  | kA |  |  |  |  | Trefoil wtihstrand force | [5 empty] | #REF!
| - Lineal spacing (D) |  |  |  | 600 |  | mm |  |  |  |  | Flat force withstrand force
g. | Formation |  |  |  | Trefoil | [6 empty] | ขอย้ายไปด้านบนได้ไหม
| Note [1]: | The exact size of Cable Cleat shall be confirmed after the exact overall diameter of XLPE power cable is confirmed during project stage. | [9 empty] | เพิ่มเพื่อความชัดเจน
| Note [2]: | Definitions comply with IEC 61914. metallic consisting of metal only. composite consisting of metallic and non-metallic materials.
a) Fibre reinforced resin materials are not considered to be composite.
b) Materials include any materials supplied by the manufacturer as part of a cable cleat or intermediate restraint or with a cable cleat or intermediate restraint in the same packaging. This may include fixings such as nuts, bolts, screws, washers, springs and pins.
| Note [3]: | The data specified in this item shall conform to the Type Test Report of the type proposed.
| Note [4]: | The values shall be based on the same cables and conditions of the test for resistance to electromechanical forces specified in IEC 61914.
| conforming with EGAT requirement (IEC 61914) |  |  | Trefoil
| Other |  |  | Flat
Metallic
| Composite |  |  | X