## outdr ter 33blow
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | The Consortium of Siemens Energy Limited and RSS 2016 Public Company Limited |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | 3M
|  | - Country of origin |  | USA
b. | Type / Model / Cat. NO. |  |  | Cold Shrink/QT-II 5652/No1
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Silicone Rubber
e. | Rated Voltage |  |  | Insulation Class 25 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 21.5 |  |  |  | kV
i. | Operating Environments |  |  | Heavy Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 35 | mm2 |  | Max | 120 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 21.3 | mm |  | Max | 35 | mm
Note: Although the conductor size range in this proposal does not conform to the XLPE proposal data, the cable termination is still suitable for use with the proposed XLPE cables.
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X