## XLPE
115 kV and below XLPE POWER CABLE
FORM PD 322
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB17
BIDDER |  | LOXLEY POWER SYSTEMS COMPANY LIMITED |  |  | ITEM NO. |  | 1AB17-1
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  |  | Charoong Thai Wire & Cable Public Co., Ltd.
|  | - Country of origin |  |  | Thailand
b. | Type / Model / Cat. NO. |  |  |  | CU/XLPE/PVC 22 kV
c. | Applied Standard |  |  |  | conforming with EGAT requirement ( ICEA Pub. No S-93-639)
*in case of other, please specify in the box below :
d. | Voltage Class |  |  |  | 22 |  |  |  |  | kV
e. | Calculated Cross-Sectional Area of Stranded Conductor |  |  |  | 35 |  |  |  |  | mm2
|  | - Material of Conductor |  |  | Plain Annealed Copper
|  | - No. of Wires in the Stranded Conductor |  |  | 7
|  | - Diameter of Each Wire |  |  | 2.65 |  |  |  |  | mm
f. | Outside Diameter of Stranded Conductor |  |  |  | Min | 6.88 | mm |  | Max | 7.02 | mm
g. | Conductor Screen |  | (Material / Thickness) |  | Semi-conducting cross-linked Polyethylene |  |  |  | / | 0.6 | mm
h. | Insulation |  | (Material / Thickness) |  | Cross-linked Polyethylene (XLPE) |  |  |  | / | 8.76 | mm
i. | Insulation Screen |  | (Material / Thickness) |  | Semi-conducting cross-linked Polyethylene |  |  |  | / | 0.6 | mm
j. | Outside Diameter of Insulation with |  |  |  | Min | 23.6 | mm |  | Max | 28 | mm
Extruded Semi-Conducting Insulation Screen (min-max)
k. | Metal Screen/Sheath |  | (Material / Thickness) |  | Annealed Copper Tape |  |  |  | / | 0.1 | mm
l. | Cushion |  | (Material / Thickness) |  | Polyester nonwoven tape |  |  |  | / | 0.26 | mm
m. | Oversheath (Jacket) |  | (Material / Thickness) |  | Polyvinyl chloride (PVC) ; Black |  |  |  | / | 2.03 | mm
n. | Overall Diameter (min-max) |  |  |  | Min | 32 | mm |  | Max | 35 | mm
o. | Impulse Withstand Voltage (BIL) |  |  |  | 150 | [5 empty] | kV
p. | (1) Ampacity of conductor in Free Air, Flat Formation with Spacing 1 Time Diameter [1] | [7 empty] | 190 |  | A
| (2) Ampacity of conductor for Direct Burial, Flat Formation with Spacing 1 Time Diameter, | [7 empty] | 155 |  | A
Depth of Laying in Ground 0.4 m, Soil Thermal Resistivity 1.2°C-m/watt [1]
q. | Min Bending Radius as a Multiple of Cable Diameter
|  | - During installation |  |  | 20D |  |  |  |  | Times
|  | - After Installation |  |  | 10D |  |  |  |  | Times
r. | Max Resistance at 20 °C of Conductor |  |  |  | 0.524 |  |  |  |  | Ω/km
s. | Length of Cable per Reel |  |  |  | 500 |  |  |  |  | m
Note [1]: |  | Conductor Temperature not in Excess of 90°C at 100% Load Factor and at an Ambient Temperature of 45°C
Note [2]: |  | Drawing and dimension of Cable Reels/Drums together with packing details shall be submitted during project stage for EGAT approval.
conforming with EGAT requirement ( ICEA Pub. No S-93-639)
conforming with EGAT requirement (TIS 2202)
conforming with EGAT requirement (IEC 62067)
Other*