## GIS-1AB7_SIEMENS ENE (hidden)
SF6 GAS INSULATED SWITCHGEAR (GIS)
FORM PD 170
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 |  |  |  | SCHEDULE NO | [5 empty] | 1AB7, 1D7
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  |  |  |  | ITEM NO |  |  |  |  | 1AB7-1 to 1AB7-11 / 2D7-1 to 2D7-9
a. | GIS Manufacturer / country of origin | [5 empty] | Siemens High Voltage Switchgear Co., Ltd. Shanghai /China
| GIB Manufacturer / country of origin | [5 empty] | Siemens High Voltage Switchgear Co., Ltd. Shanghai/China
b. | Type | [5 empty] | 8DN8, SF6 Gas-insulated
c. | Applied standards | [5 empty] | IEC62271-1 & IEC62271-203
d. | General rating
| - Rated voltage | [5 empty] | 145 | [12 empty] | kV
| - Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
| - Rated frequency | [5 empty] | 50 | [12 empty] | Hz
| - Power frequency withstand level | [5 empty] | 275 | [12 empty] | kV
| - Lightning impulse withstand level | [5 empty] | 650 | [12 empty] | kV
| - Switching impulse withstand level | [5 empty] | N/A | [12 empty] | kV
- Rated continuous current
| - Busbars | [5 empty] | 3150 | [12 empty] | A
| - Feeder | [5 empty] | 3150 | [12 empty] | A
- Rated short-time (1s) withstand current for
| main and earthing circuits | [5 empty] | 40 | [12 empty] | kA
- Rated peak withstand current for main and
| earthing circuits | [5 empty] | 100 | [12 empty] | kA
e. | Type of enclosure | [6 empty] | Single phase enclosure
[7 empty] | X | Three phase enclosure
f. | Material
| - Enclosure | [5 empty] | AL-Alloy
| - Conductor | [5 empty] | AL-Alloy
g. | Conductor connecting piece
| - Type | [5 empty] | Plug-in by u-sing coupling contacts
| - Material | [5 empty] | AL or CU Plated
h. | SF6 Gas
| - Compliance to IEC 60376 | [5 empty] | X | Yes | [5 empty] | No
| - Manufacturer | [5 empty] | Kemeite/China
| - Purity by weight | [5 empty] | > 99.7 | [12 empty] | %
| - Maximum moisture content | [5 empty] | 25 | [12 empty] | ppm
Gas Compartments
SF6 pressure information |  |  | Unit | CB | Adjacent CB | Others
[6 empty] | VT |  | Others |  |  |  |  | adjacent VT |  |  |  | ……..
Rated filling pressure at 20 oC |  |  | Bar | 5.6 | 4.5 | 5.6 |  | 4.5 |  |  |  |  | 4.5 |  |  |  | ……..
Alarm pressure at 20 oC |  |  | Bar | 5.2/5.0 | 4.2/4.0/52 | 5.2/5.0 |  | 4.2/4.0 |  |  |  |  | 4.2/4.0/5.2 |  |  |  | ……..
Minimum functional pressure at 20 oC |  |  | Bar | 5 | 4 | 5 |  | 4 |  |  |  |  | 4 |  |  |  | ……..
Design pressure of enclosures |  |  | Bar | 8 | 6 | 8 |  | 6 |  |  |  |  | 6 |  |  |  | ……..
Operating pressure of pressure relief device |  |  | Bar | 9.4-10.4 | 8.45-9.35 | 9.4-10.4 |  | 8.45-9.35 |  |  |  |  | 8.45-9.35 |  |  |  | ……..
| - Pressure information in table above is given in | [5 empty] | X | Relative | [5 empty] | Absolute
| - Internal fault Short-circuit current | [5 empty] | 40 | [12 empty] | kA
- Weight of SF6 gas filling
| - Complete GIS | [5 empty] | Approx.5100(It may be changed after design freeze) | [12 empty] | kg
| - The largest compartment | [5 empty] | <=150 | [12 empty] | kg
| - SF6 gas leakage rate | [5 empty] | <0.5 as per IEC | [12 empty] | %/year
(Certified test record shall be submitted together with tender document
during the bidding as an evidence for consideration of evaluation)
i. | Rated supply voltage of closing and opening devices | [5 empty] | 125 | [12 empty] | Vdc
and auxiliary circuits
j. | Temperature limitations for
| - Gas dew point | [5 empty] | -5 as per IEC | [12 empty] | °C
| - Buses and connections | [5 empty] | Max.115(inner conductor) | [12 empty] | °C
| - External parts subjected to contact by personnel | [5 empty] | Max 80, no touch expected on enclusure | [12 empty] | °C
k. | Minimum bay to bay spacing (metal-to-metal) | [5 empty] | As per layout drawing | [12 empty] | mm*
| NB * | If EGAT considers that the specified clearance from bay to bay is inadequate for breaker maintenance, the Bidder shall be responsible for an appropriate and acceptable modification of such clearance without any price increase.
l. | Constructional features
| - Mass of the heaviest transport unit | [5 empty] | Approx. 3500 | [12 empty] | kg
| - Length of longest section for transportation | [5 empty] | Approx.8m. (Max. Length: GIB + angle ) | [12 empty] | m
m. | Busducts
| - Type | [5 empty] | 3-ph enclosed
| - Minimum clearance to earth | [5 empty] | ~49 | [12 empty] | mm
| - Span between busbar supports | [5 empty] | Depends on specific project | [12 empty] | mm
| - Inductance | [5 empty] | 0.2±0.04μH/m | [12 empty] | H/m
| - Capacitance | [5 empty] | 90±18 | [12 empty] | pF/m
| - Resistance of enclosure at rated frequency | [5 empty] | ~9 uΩ/m | [12 empty] | W/m
| - Resistance of conductor at rated frequency | [5 empty] | ~8 uΩ/m | [12 empty] | W/m
| - Surge impedance | [5 empty] | 47±10Ω
n. | Space Heating
| - Install heating | [5 empty] | CB：~26/per PCS | [12 empty] | W
| - Number of heater | [5 empty] | CB：3
| - Rated voltage | [5 empty] | AC230 | [12 empty] | V
Circuit Breaker
a. | Type | [5 empty] | SF6 gas insulated, indoor Spring Drive
b. | Single pole and/or three pole operation | [5 empty] | 3-pole group operated
c. | Number of breaks per pole | [5 empty] | 1
d. | Alignment of Circuit Breaker | [5 empty] | X | Vertical | [5 empty] | Horizontal
e. | Type of interrupter | [5 empty] | X | Self blast | [5 empty] | Puffer
Etc.
f. | Applied standard | [5 empty] | IEC 62271-100
g. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
h. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
i. | First pole to clear factor | [5 empty] | 1.3
j. | Power frequency withstand voltage
| - Across open switching device | [5 empty] | 315 | [12 empty] | kV
| - Phase to earth | [5 empty] | 275 | [12 empty] | kV
k. | Lightning impulse withstand voltage
| - Across open switching device | [5 empty] | 750 | [12 empty] | kV
| - Phase to earth | [5 empty] | 650 | [12 empty] | kV
l. | Switching impulse withstand voltage
| - Between phases | [5 empty] | N/A | [12 empty] | kV
| - Phase-to-earth and across open switching device | [5 empty] | N/A | [12 empty] | kV
m. | Frequency | [5 empty] | 50 | [12 empty] | Hz
n. | Current rating
| - Rated continuous | [5 empty] | 3150 | [12 empty] | A
| - Rated short circuit current at max kV | [5 empty] | 40 | [12 empty] | kA
| - Limited overload capacity | [5 empty] | 3150 | [12 empty] | A
o. | Interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 46.4 | [12 empty] | kA
| - 1 s short time current | [5 empty] | 40 | [12 empty] | kA
- Max opening and interrupting time at rated voltage
| - Opening time | [5 empty] | 32±3 | [12 empty] | ms
| - Interrupting time | [5 empty] | 54.2 | [12 empty] | ms
| - Current at max interrupting time | [5 empty] | 40000(short circuit current) | [12 empty] | A
| - Interrupting time of resistive current | [5 empty] | 54.2 | [12 empty] | ms
| - Mechanism stroke | [5 empty] | 120(output stroke) | [12 empty] | mm
| - Interrupter stroke | [5 empty] | 120(moving contacts) | [12 empty] | mm
| - Opening velocity (contact part) | [5 empty] | 5.06 | [12 empty] | m/s
p. | Asymmetrical interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 46.4 | [12 empty] | kA
q. | Closing rating
| - Closing and latching current at max kV | [5 empty] | 40 | [12 empty] | kA
| - Making capacity-peak at max kV | [5 empty] | 100 | [12 empty] | kA
| - Closing time at rated operations | [5 empty] | 55±6 | [12 empty] | ms
| - Closing velocity (contact touch) | [5 empty] | 4.06 | [12 empty] | m/s
r. | Capacitive current
| - Rated capacitance current switching | [5 empty] | Unload line:0.05,unload cable:0.16 | [12 empty] | kA
| - Corresponding to max line length of | [5 empty] | as per IEC | [12 empty] | km
| - Rated transient overvoltage factor | [5 empty] | C2-class capacitive currents switch without restrikes and switching over-voltage under rated duties.
s. | Temperature rise of contacts at nominal current | [5 empty] | Follows IEC62271-1 | [12 empty] | °C
t. | Operating mechanism | [5 empty] | Closing | [6 empty] | Tripping
| - Manufacturer type | [5 empty] | 8DN8,FA2 (common drive, 3 pole group operated)
| - Mechanism type (spring, hydraulic, etc) | [5 empty] | Spring | [6 empty] | Spring
| - Operating voltage range (min/max) | [5 empty] | 106.25 |  | / | 137.5 |  |  |  | 87.5 |  |  | / | 137.5 |  | Vdc
| - Current rating of coil | [5 empty] | 2.5 | [6 empty] | 2.5 | [5 empty] | A
| - Command duration | [5 empty] | 55± 6 | [6 empty] | 32± 3 | [5 empty] | ms
u. | Reclosing duty cycle | [5 empty] | O-0.3s-CO-180s-CO
v. | Number of operations between servicing | [5 empty] | 6000 at rated current
w. | Rated reclosing time | [5 empty] | 355 | [12 empty] | ms
x. | Net weight of each breaker | [5 empty] | ~908 | [12 empty] | kg
y. | Weight of SF6 gas filling for each breaker | [5 empty] | ~44 (with CT) | [12 empty] | kg
z. | Spring charged mechanism
| - Model no | [5 empty] | FA2 (3-pole group operated type)
| - Motor rating | [5 empty] | 687.5 | [5 empty] | W | 125 | [5 empty] | Vdc
| - Max charging time at rated voltage | [5 empty] | 15 | [12 empty] | s
aa. | Air compressor set or hydraulic oil pump
| - Manufacturer / country of origin | [5 empty] | N.A
| - Model no | [5 empty] | N.A
| - Number per breaker | [5 empty] | N.A
| - Capacity of each set | [5 empty] | N.A | [12 empty] | Litre
| - Operating pressure | [5 empty] | N.A | [12 empty] | bar
| - Motor rating | [5 empty] | N.A |  |  | W |  | N.A | Phase |  |  | N.A |  |  | V | N.A | Hz
| - Net weight of each set | [5 empty] | N.A | [12 empty] | kg
| - Overall height | [5 empty] | N.A | [12 empty] | mm
| - Base dimensions | [5 empty] | N.A | [11 empty] | mmxmm
ab. | Air storage tank or hydraulic accumulator
| - Number per breaker | [5 empty] | N.A
| - Capacity of each set | [5 empty] | N.A | [12 empty] | Litre
| - Working pressure | [5 empty] | N.A | [12 empty] | bar
| - Net weight of each set | [5 empty] | N.A | [12 empty] | kg
| - Dimensions, diameter x length | [5 empty] | N.A | [11 empty] | mmxmm
ac. | Stored energy requirements | [5 empty] | O-CO
ad. | Max recharging time after CO operation | [5 empty] | 15 | [12 empty] | s
Disconnecting Switch
a. | Type | [5 empty] | 3-phase group operated
b. | Number of breaks per pole | [5 empty] | 1
c. | Applied standard | [5 empty] | IEC62271-102
d. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
e. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
f. | Power frequency withstand voltage
| - Across isolating distance | [5 empty] | 315 | [12 empty] | kV
| - Phase-to-earth | [5 empty] | 275 | [12 empty] | kV
g. | Lightning impulse withstand voltage
| - Across isolating distance | [5 empty] | 750 | [12 empty] | kV
| - Phase-to-earth | [5 empty] | 650 | [12 empty] | kV
h. | Switching impulse withstand voltage
| - Across isolating distance | [5 empty] | N.A | [12 empty] | kV
| - Between phases | [5 empty] | N.A | [12 empty] | kV
| - Phase-to-earth | [5 empty] | N.A | [12 empty] | kV
i. | Frequency | [5 empty] | 50 | [12 empty] | Hz
j. | Rated continuous current | [5 empty] | 3150 | [12 empty] | A
k. | Rated peak withstand current | [5 empty] | 100 | [12 empty] | kA
l. | Rated short time (1 s) withstanding current | [5 empty] | 40 | [12 empty] | kA
m. | Type of contact | [5 empty] | Pin (moving contact)
n. | Material of contact | [5 empty] | AL or CU with Silver Plated (moving contact)
o. | Thickness of silver on contact surfaces | [5 empty] | ~9 | [12 empty] | mm
p. | Voltage drop across contacts at rated normal current | [5 empty] | ~2.2 | [12 empty] | mV
q. | Operating mechanism | [5 empty] | Motor and emergency manual operation
r. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
s. | Motor Drive mechanism
| - Model no | [5 empty] | 8D type, DC control type
| - Motor rating | [5 empty] | 120 | [5 empty] | W | 125 | [5 empty] | Vdc
t. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | Contact operating time: around 1.50 s/Motor operating time: <3 |  |  |  | / | Contact operating time: around 1.10 s/Motor |  |  | / | Contact operating time: around 1 s/Motor operating |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | Contact operating time: around 1.50 s/Motor operating time: <3 |  |  |  | / | Contact operating time: around 1.10 s/Motor |  |  | / | Contact operating time: around 1 s/Motor operating |  |  |  | s
High Speed Grounding Switch
a. | Type | [5 empty] | 3-phase group operated
b. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 275 | [12 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 750 | [12 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | N/A | [12 empty] | kV
f. | Rated short circuit making current | [5 empty] | 100 | [12 empty] | kA
g. | Rated short time (1 s) withstand current | [5 empty] | 40 | [12 empty] | kA
h. | Type of contact | [5 empty] | Pin (Moving Contact)
i. | Material of contacts | [5 empty] | Cu silver-plated(fixed contact) Cu with copper tungsten(moving contact)
j. | Thickness of silver on contacts surfaces | [5 empty] | ~9 | [12 empty] | mm
k. | Operating mechanism | [5 empty] | Motorized Spring and manual operation for closing Motorized and manual operation for opening
l. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
m. | Motor Drive mechanism
| - Model no | [5 empty] | 8D type,DC control type
| - Motor rating | [5 empty] | 200 | [5 empty] | W | 125 | [5 empty] | Vdc
n. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | Contact operating time: around 4.3 s /Motor operating time: <6 s, |  |  |  | / | Contact operating time: around 3.5 s /Motor |  |  | / | Contact operating time: around 3.2 s /Motor |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | Contact operating time: around 3.9 s/Motor operating time: <6 s, |  |  |  | / | Contact operating time: around 2.8 s/Motor |  |  | / | Contact operating time: around 2.4 s/Motor operating |  |  |  | s
Maintenance Grounding Switch
a. | Type | [5 empty] | 3-phase group operated
b. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 275 | [12 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 650 | [12 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | N/A | [12 empty] | kV
f. | Rated short time (1 s) withstand current | [5 empty] | 40 | [12 empty] | kA
g. | Type and material of contacts | [5 empty] | Pin(moving contact)/AL Silver Plated
h. | Operating mechanism | [5 empty] | Motorized and emergency manual operation
i. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
j. | Motor Drive mechanism
| - Model no | [5 empty] | 8D type, DC control type
| - Motor rating | [5 empty] | 200 | [5 empty] | W | 125 | [5 empty] | Vdc
j. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | Contact operating time: around 1.5 s/ Motor operating time: < 3 |  |  |  | / | Contact operating time: around 1.10 s/ Motor |  |  | / | Contact operating time: around 0.95 s/ Motor |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | Contact operating time: around 1.5 s/ Motor operating time: < 3 |  |  |  | / | Contact operating time: around 1.10 s/ Motor |  |  | / | Contact operating time: around 0.95s/ Motor |  |  |  | s
Voltage Transformer
a. | Manufacturer/ Country | [5 empty] | Sieyuan/China or Nissin/China
b. | Type / Model / Catalog No. | [5 empty] | Inductive/JSQXFH-110(Sieyuan) or / SVTR-10C(3Phases) (Nissin)/ or SVR-10C Code D(Nissin)
c. | Applied standard | [5 empty] | IEC61869-3
d. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
e. | Rated primary voltage | [5 empty] | 115/√3 | [12 empty] | kV
f. | Voltage ratio | [5 empty] | 577/1,000 & 577/1,000:1
g. | Secondary voltage rating
| - No 1 secondary winding | [5 empty] | 115/66.4
| - No 2 secondary winding | [5 empty] | 115/66.4
h. | Burden
| - No 1 secondary winding | [5 empty] | 30VA for 3P, 0-15 VA for 0.2&3P
| - No 2 secondary winding | [5 empty] | 30VA for 3P, 0-15 VA for 0.2&3P
| - Simultaneous | [5 empty] | 30VA
i. | Accuracy class | [5 empty] | 3P/3P; 0.2&3P/0.2&3P
Current Transformer
a. | Manufacturer/ Country | [5 empty] | Sihui/China
b. | Type / Model / Catalog No. | [5 empty] | Inductive / LMGB-110
c. | Applied standard | [5 empty] | IEC61869-2
d. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
e. | Rated Primary Current | [5 empty] | 2000 for 5P20; 600/1200 for 0.2S | [12 empty] | A
f. | Rated Secondary Current | [5 empty] | 1 | [12 empty] | A
g. | No of core | [5 empty] | 4 for 5P20, 2 for 0.2S
h. | Current ratio | [5 empty] | 300/400/500/800/1100/1200/1500/1600/2000:1//1//1//1 for 5P20, 600/1200:1//1 for 0.2S
i. | Accuracy class | [5 empty] | 5P20, 20VA ( Protection), 0.2S, 20VA (Metering)
j. | Continuous thermal current rating factor | [5 empty] | 100% for All
Surge Arrester
a. | Manufacturer/ Country | [5 empty] | N/A
b. | Type / Model / Catalog No. | [5 empty] | N/A
c. | Applied standard | [5 empty] | N/A
d. | Maximum service voltage | [5 empty] | N/A | [12 empty] | kV
e. | Class | [5 empty] | N/A
f. | Duty cycle current | [5 empty] | N/A | [12 empty] | kA
g. | Arrester insulation withstand, BIL | [5 empty] | N/A | [12 empty] | kV
h. | Maximum continuous operating voltage (Uc) | [5 empty] | N/A | [12 empty] | kV
i. | Maximum equivalent front-of-wave protective level | [5 empty] | N/A | [12 empty] | kV
j. | Maximum discharge voltage at 5/10/20 kA | [5 empty] | N/A | [12 empty] | kV
k. | Net weight of each arrester | [5 empty] | N/A | [12 empty] | kg
Bushing
a. | Manufacturer/ Country | [5 empty] | XD/China
b. | Type / Model / Catalog No. | [5 empty] | SF6 to air
c. | Applied standard | [5 empty] | IEC60137
d. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
e. | Type of internal insulation | [5 empty] | SF6 gas
f. | Type of external insulation | [5 empty] | Procelain
g. | Nominal specific creepage distance | [5 empty] | 25 at least | [12 empty] | mm/kV
h. | Cantilever load | [5 empty] | 4000 | [12 empty] | N
i. | Type of line termination | [5 empty] | Terminal plate, Terminal connector suitable for 4 x 1272 MCM ACSR (supplied by main contractor)
SF6 Service and Storage Unit
a. Type | [6 empty] | N/A
b. Compression pressure | [6 empty] | N/A | [12 empty] | bar
c. Suction rate | [6 empty] | N/A | [12 empty] | m3/hr.
d. SF6 gas recovery down to | [6 empty] | N/A | [12 empty] | mbar
e. Vacuum pump rate | [6 empty] | N/A | [12 empty] | m3/hr.
f. Final vacuum down to | [6 empty] | N/A | [12 empty] | mbar
SF6 gas filling cart
a. Vacuum pump rate | [6 empty] | 16 | [12 empty] | m3/hr.
b. Evacuate rate down to | [6 empty] | <=1 | [12 empty] | mbar
c. The weighing scale
- Range | [6 empty] | 0-150 | [12 empty] | kg
- Accuracy | [6 empty] | +/-20 | [12 empty] | g
d. Pressure reducer for SF6 | [6 empty] | 0-1 Mpa,0-10 | [12 empty] | bar
Portable SF6 gas leak detector
a. Sensitivity | [6 empty] | N/A | [12 empty] | ppmv
b. Accuracy | [6 empty] | N/A | [10 empty] | % of full scale
c. Digit display | [7 empty] | Yes | [5 empty] | No
SF6 gas quality measuring device
a. | Moisture content
| - Range of DEW point | [5 empty] | N/A | [12 empty] | oC
| - Accuracy | [5 empty] | N/A | [12 empty] | oC
| - Pump back function | [6 empty] | Yes | [5 empty] | No
b. | SF6 content
| - Range | [5 empty] | N/A | [11 empty] | % volume
| - Accuracy | [5 empty] | N/A | [11 empty] | % volume
Gas decomposition tester
a. | SO2
| - Range | [5 empty] | N/A | [12 empty] | ppmv
| - Acuuracy | [5 empty] | N/A | [12 empty] | %

## GIS1AB7_Hitachi Ene (hidden)
SF6 GAS INSULATED SWITCHGEAR (GIS)
FORM PD 170
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 |  |  |  | SCHEDULE NO | [5 empty] | 1AB7, 1D7
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  |  |  |  | ITEM NO |  |  |  |  | 1AB7-1 to 1AB7-9 and 1D7-1 to 1D7-7
a. | GIS Manufacturer / country of origin | [5 empty] | Hitachi Energy High Voltage Switchgear (Xiamen) Company Limited/China
| GIB Manufacturer / country of origin | [5 empty] | Hitachi Energy High Voltage Switchgear (Xiamen) Company Limited/China
b. | Type | [5 empty] | ELK-04
c. | Applied standards | [5 empty] | IEC62271-203
d. | General rating
| - Rated voltage | [5 empty] | 145 | [12 empty] | kV
| - Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
| - Rated frequency | [5 empty] | 50 | [12 empty] | Hz
| - Power frequency withstand level | [5 empty] | 275 | [12 empty] | kV
| - Lightning impulse withstand level | [5 empty] | 650 | [12 empty] | kV
| - Switching impulse withstand level | [5 empty] | N/A | [12 empty] | kV
- Rated continuous current
| - Busbars | [5 empty] | 2500 | [12 empty] | A
| - Feeder | [5 empty] | 2500 | [12 empty] | A
- Rated short-time (1s) withstand current for
| main and earthing circuits | [5 empty] | 40 | [12 empty] | kA
- Rated peak withstand current for main and
| earthing circuits | [5 empty] | 100 | [12 empty] | kA
e. | Type of enclosure | [6 empty] | Single phase enclosure
[7 empty] | X | Three phase enclosure
f. | Material
| - Enclosure | [5 empty] | Aluminum
| - Conductor | [5 empty] | Aluminum
g. | Conductor connecting piece
| - Type | [5 empty] | Tulip, Contact Spring
| - Material | [5 empty] | Silver Plated Aluminium
h. | SF6 Gas
| - Compliance to IEC 60376 | [5 empty] | X | Yes | [5 empty] | No
| - Manufacturer | [5 empty] | Chengdu Kemeite Flourine Industry Plastics Co.,Ltd.
| - Purity by weight | [5 empty] | 99.8 | [12 empty] | %
| - Maximum moisture content | [5 empty] | 25 ppmw | [12 empty] | ppm
Gas Compartments
SF6 pressure information |  |  | Unit | CB | Adjacent CB | Others
[6 empty] | except VT |  | VT |  |  |  |  | Unit |  |  |  | ……..
Rated filling pressure at 20 oC |  |  | Bar | 7 | 6 | 6 |  | 7 |  |  |  |  | Bar (abs) |  |  |  | ……..
Alarm pressure at 20 oC |  |  | Bar | 6.2/6 | 6.3/5.4/5.2 | 5.4/5.2 |  | 6.2/6 |  |  |  |  | Bar (abs) |  |  |  | ……..
Minimum functional pressure at 20 oC |  |  | Bar | 6 | 5.2 | 5.2 |  | 6 |  |  |  |  | Bar (abs) |  |  |  | ……..
Design pressure of enclosures |  |  | Bar | 7.5 | 6.3 | 6.3 |  | 7.5 |  |  |  |  | Bar (rel) |  |  |  | ……..
Operating pressure of pressure relief device |  |  | Bar | 10.2+/-10% | 10.2+/-10% | 10.2+/-10% |  | 10.2+/-10% |  |  |  |  | Bar (rel) |  |  |  | ……..
| - Pressure information in table above is given in | [6 empty] | Relative | [5 empty] | Absolute |  |  |  | *See Unit
| - Internal fault Short-circuit current | [5 empty] | 40 | [12 empty] | kA
- Weight of SF6 gas filling
| - Complete GIS | [5 empty] | 4800 (estimate) | [12 empty] | kg
| - The largest compartment | [5 empty] | 46 | [12 empty] | kg
| - SF6 gas leakage rate | [5 empty] | < 0.5 | [12 empty] | %/year
(Certified test record shall be submitted together with tender document
during the bidding as an evidence for consideration of evaluation)
i. | Rated supply voltage of closing and opening devices | [5 empty] | 125 | [12 empty] | Vdc
and auxiliary circuits
j. | Temperature limitations for
| - Gas dew point | [5 empty] | -10 (According to IEC62271-1, Caluse 11.3.6) | [12 empty] | °C
| - Buses and connections | [5 empty] | Temp rise 65 °C (Indoor), 60 °C (Outdoor) | [12 empty] | °C
| - External parts subjected to contact by personnel | [5 empty] | Temp rise 30 °C (Indoor), 25 °C (Outdoor) | [12 empty] | °C
k. | Minimum bay to bay spacing (metal-to-metal) | [5 empty] | 1094 | [12 empty] | mm*
| NB * | If EGAT considers that the specified clearance from bay to bay is inadequate for breaker maintenance, the Bidder shall be responsible for an appropriate and acceptable modification of such clearance without any price increase.
l. | Constructional features
| - Mass of the heaviest transport unit | [5 empty] | 3000 (estimate) | [12 empty] | kg
| - Length of longest section for transportation | [5 empty] | 4.5 | [12 empty] | m
m. | Busducts
| - Type | [5 empty] | ELK-04
| - Minimum clearance to earth | [5 empty] | 38 | [12 empty] | mm
| - Span between busbar supports | [5 empty] | Up to 4000 | [12 empty] | mm
| - Inductance | [5 empty] | 275x109 | [12 empty] | H/m
| - Capacitance | [5 empty] | 70 | [12 empty] | pF/m
| - Resistance of enclosure at rated frequency | [5 empty] | 5e-06 | [12 empty] | W/m
| - Resistance of conductor at rated frequency | [5 empty] | 1e-05 | [12 empty] | W/m
| - Surge impedance | [5 empty] | 65Ω
n. | Space Heating
| - Install heating | [5 empty] | 70 | [12 empty] | W
| - Number of heater | [5 empty] | Each operating mechanism and LCP
| - Rated voltage | [5 empty] | 230 | [12 empty] | V
Circuit Breaker
a. | Type | [5 empty] | ELK-04
b. | Single pole and/or three pole operation | [5 empty] | 3-pole
c. | Number of breaks per pole | [5 empty] | 1
d. | Alignment of Circuit Breaker | [5 empty] | X | Vertical | [5 empty] | Horizontal
e. | Type of interrupter | [5 empty] | X | Self blast | [5 empty] | Puffer
Etc.
f. | Applied standard | [5 empty] | IEC62271-100
g. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
h. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
i. | First pole to clear factor | [5 empty] | 1.5
j. | Power frequency withstand voltage
| - Across open switching device | [5 empty] | 315 | [12 empty] | kV
| - Phase to earth | [5 empty] | 275 | [12 empty] | kV
k. | Lightning impulse withstand voltage
| - Across open switching device | [5 empty] | 750 | [12 empty] | kV
| - Phase to earth | [5 empty] | 650 | [12 empty] | kV
l. | Switching impulse withstand voltage
| - Between phases | [5 empty] | N/A | [12 empty] | kV
| - Phase-to-earth and across open switching device | [5 empty] | N/A | [12 empty] | kV
m. | Frequency | [5 empty] | 50 | [12 empty] | Hz
n. | Current rating
| - Rated continuous | [5 empty] | 2500 | [12 empty] | A
| - Rated short circuit current at max kV | [5 empty] | 40 | [12 empty] | kA
| - Limited overload capacity | [5 empty] | N/A | [12 empty] | A
o. | Interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 48.7(49.1%DC) | [12 empty] | kA
| - 1 s short time current | [5 empty] | 40 | [12 empty] | kA
- Max opening and interrupting time at rated voltage
| - Opening time | [5 empty] | 22~38 | [12 empty] | ms
| - Interrupting time | [5 empty] | 36~60 | [12 empty] | ms
| - Current at max interrupting time | [5 empty] | 40k | [12 empty] | A
| - Interrupting time of resistive current | [5 empty] | 26~60 | [12 empty] | ms
| - Mechanism stroke | [5 empty] | 115 | [12 empty] | mm
| - Interrupter stroke | [5 empty] | 110 | [12 empty] | mm
| - Opening velocity (contact part) | [5 empty] | 4.8~5.8 | [12 empty] | m/s
p. | Asymmetrical interrupting rating
| - Max asymmetrical interrupting current | [5 empty] | 48.7(49.1%DC) | [12 empty] | kA
q. | Closing rating
| - Closing and latching current at max kV | [5 empty] | 40 | [12 empty] | kA
| - Making capacity-peak at max kV | [5 empty] | 100 | [12 empty] | kA
| - Closing time at rated operations | [5 empty] | 43~65 | [12 empty] | ms
| - Closing velocity (contact touch) | [5 empty] | 2.8~3.6 | [12 empty] | m/s
r. | Capacitive current
| - Rated capacitance current switching | [5 empty] | 50A(Line), 160A(Cable) | [12 empty] | kA
| - Corresponding to max line length of | [5 empty] | approx. 150 | [12 empty] | km
| - Rated transient overvoltage factor | [5 empty] | 1.4
s. | Temperature rise of contacts at nominal current | [5 empty] | 65 | [12 empty] | °C
t. | Operating mechanism | [5 empty] | Closing | [6 empty] | Tripping
| - Manufacturer type | [5 empty] | HMB
| - Mechanism type (spring, hydraulic, etc) | [5 empty] | Spring (Hydromechanical) | [6 empty] | Spring (Hydromechanical)
| - Operating voltage range (min/max) | [5 empty] | 90 |  | / | 140 |  |  |  | 70 |  |  | / | 140 |  | Vdc
| - Current rating of coil | [5 empty] | 6 | [6 empty] | 6 | [5 empty] | A
| - Command duration | [5 empty] | Approx. 20 | [6 empty] | Approx. 20 | [5 empty] | ms
u. | Reclosing duty cycle | [5 empty] | O－0.3 s－CO－3 min－CO
v. | Number of operations between servicing | [5 empty] | 2000
w. | Rated reclosing time | [5 empty] | 300 | [12 empty] | ms
x. | Net weight of each breaker | [5 empty] | Approx. 800 | [12 empty] | kg
y. | Weight of SF6 gas filling for each breaker | [5 empty] | 46 | [12 empty] | kg
z. | Spring charged mechanism
| - Model no | [5 empty] | N/A
| - Motor rating | [5 empty] | N/A | [5 empty] | W | N/A | [5 empty] | Vdc
| - Max charging time at rated voltage | [5 empty] | N/A | [12 empty] | s
aa. | Air compressor set or hydraulic oil pump
| - Manufacturer / country of origin | [5 empty] | Hitachi Energy High Voltage Switchgear (Xiamen) Company Limited/China
| - Model no | [5 empty] | HMB
| - Number per breaker | [5 empty] | 1
| - Capacity of each set | [5 empty] | Approx. 1.5 | [12 empty] | Litre
| - Operating pressure | [5 empty] | 468~528 | [12 empty] | bar
| - Motor rating | [5 empty] | 660 |  |  | W |  |  | Phase |  |  | 220 |  |  | V |  | Hz
(Provide AC to DC supply converter in LCC)
| - Net weight of each set | [5 empty] | Approx. 300 | [12 empty] | kg
| - Overall height | [5 empty] | 390 | [12 empty] | mm
| - Base dimensions | [5 empty] | 890x745 | [11 empty] | mmxmm
ab. | Air storage tank or hydraulic accumulator
| - Number per breaker | [5 empty] | N/A
| - Capacity of each set | [5 empty] | N/A | [12 empty] | Litre
| - Working pressure | [5 empty] | N/A | [12 empty] | bar
| - Net weight of each set | [5 empty] | N/A | [12 empty] | kg
| - Dimensions, diameter x length | [5 empty] | N/A | [11 empty] | mmxmm
ac. | Stored energy requirements | [5 empty] | OCO
ad. | Max recharging time after CO operation | [5 empty] | 15 | [12 empty] | s
Disconnecting Switch
a. | Type | [5 empty] | ELK-04
b. | Number of breaks per pole | [5 empty] | 1
c. | Applied standard | [5 empty] | IEC62271-102
d. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
e. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
f. | Power frequency withstand voltage
| - Across isolating distance | [5 empty] | 315 | [12 empty] | kV
| - Phase-to-earth | [5 empty] | 275 | [12 empty] | kV
g. | Lightning impulse withstand voltage
| - Across isolating distance | [5 empty] | 750 | [12 empty] | kV
| - Phase-to-earth | [5 empty] | 650 | [12 empty] | kV
h. | Switching impulse withstand voltage
| - Across isolating distance | [5 empty] | N/A | [12 empty] | kV
| - Between phases | [5 empty] | N/A | [12 empty] | kV
| - Phase-to-earth | [5 empty] | N/A | [12 empty] | kV
i. | Frequency | [5 empty] | 50 | [12 empty] | Hz
j. | Rated continuous current | [5 empty] | 2500 | [12 empty] | A
k. | Rated peak withstand current | [5 empty] | 100 | [12 empty] | kA
l. | Rated short time (1 s) withstanding current | [5 empty] | 40 | [12 empty] | kA
m. | Type of contact | [5 empty] | Spiral (Spring) contact
n. | Material of contact | [5 empty] | Copper Silver Coated
o. | Thickness of silver on contact surfaces | [5 empty] | 0.005~0.015 | [12 empty] | mm
p. | Voltage drop across contacts at rated normal current | [5 empty] | < 80 (Reference) | [12 empty] | mV
q. | Operating mechanism | [5 empty] | Electric Motor and Emergency Manual Operation
r. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
s. | Motor Drive mechanism
| - Model no | [5 empty] | ELK-DE0
| - Motor rating | [5 empty] | 200 | [5 empty] | W | 125 | [5 empty] | Vdc
t. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | < 2.4 |  |  |  | / | < 2.4 |  |  | / | < 2.4 |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | < 1.5 |  |  |  | / | < 1.5 |  |  | / | < 1.5 |  |  |  | s
High Speed Grounding Switch
a. | Type | [5 empty] | ELK-04
b. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 275 | [12 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 650 | [12 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | N/A | [12 empty] | kV
f. | Rated short circuit making current | [5 empty] | 100 | [12 empty] | kA
g. | Rated short time (1 s) withstand current | [5 empty] | 40 | [12 empty] | kA
h. | Type of contact | [5 empty] | Tulip
i. | Material of contacts | [5 empty] | Cu-W
j. | Thickness of silver on contacts surfaces | [5 empty] | 0.005~0.015 | [12 empty] | mm
k. | Operating mechanism | [5 empty] | Electric Motor and Emergency Manual Operation
l. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
m. | Motor Drive mechanism
| - Model no | [5 empty] | ELK-ES0
| - Motor rating | [5 empty] | 150 | [5 empty] | W | 125 | [5 empty] | Vdc
n. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | < 3 (Including charge time) |  |  |  | / | < 3 (Including charge time) |  |  | / | < 3 (Including charge time) |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | < 1.5 (Including charge time) |  |  |  | / | < 1.5 (Including charge time) |  |  | / | < 1.5 (Including charge time) |  |  |  | s
Maintenance Grounding Switch
a. | Type | [5 empty] | ELK-04
b. | Rated voltage | [5 empty] | 145 | [12 empty] | kV
c. | Power frequency withstand voltage
| - Phase to earth | [5 empty] | 275 | [12 empty] | kV
d. | Lightning impulse withstand voltage
| - Phase to earth | [5 empty] | 650 | [12 empty] | kV
e. | Switching impulse withstand voltage
| - Phase to earth | [5 empty] | N/A | [12 empty] | kV
f. | Rated short time (1 s) withstand current | [5 empty] | 40 | [12 empty] | kA
g. | Type and material of contacts | [5 empty] | Spiral (Spring)/Copper Silver Coated
h. | Operating mechanism | [5 empty] | Electric Motor and Emergency Manual Operation
i. | Operating and control voltage | [5 empty] | 125 | [12 empty] | Vdc
j. | Motor Drive mechanism
| - Model no | [5 empty] | ELK-ES0
| - Motor rating | [5 empty] | 200 | [5 empty] | W | 125 | [5 empty] | Vdc
j. | Operating time
| - Closing (@min./rated/max. voltage) | [5 empty] | < 2.4 |  |  |  | / | < 2.4 |  |  | / | < 2.4 |  |  |  | s
| - Opening (@min./rated/max. voltage) | [5 empty] | < 1.5 |  |  |  | / | < 1.5 |  |  | / | < 1.5 |  |  |  | s
Voltage Transformer
a. | Manufacturer/ Country | [5 empty] | Hitachi Energy Jiangsu High Voltage Apparatus Co., Ltd. / China
b. | Type / Model / Catalog No. | [5 empty] | GVT145-EL
c. | Applied standard | [5 empty] | IEC61869, IEEE C57.13
d. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
e. | Rated primary voltage | [5 empty] | 115/√3 | [12 empty] | kV
f. | Voltage ratio | [5 empty] | 577/1000 & 577/1000:1
g. | Secondary voltage rating
| - No 1 secondary winding | [5 empty] | 115/66.4V
| - No 2 secondary winding | [5 empty] | 115/66.4V
h. | Burden
| - No 1 secondary winding | [5 empty] | 30VA for3P and 0-15VA for 0.2&3P
| - No 2 secondary winding | [5 empty] | 30 VA for 3P ; 0 - 15 VA for 0.2&3P
| - Simultaneous | [5 empty] | 30
i. | Accuracy class | [5 empty] | 3P / 3P ; 0.2&3P / 0.2&3P
Current Transformer
a. | Manufacturer/ Country | [5 empty] | Hitachi Energy Jiangsu High Voltage Apparatus Co., Ltd. / China or Guangdong Sihui Instrument Transformer Works Co., Ltd./China
b. | Type / Model / Catalog No. | [5 empty] | LMQB-145
c. | Applied standard | [5 empty] | IEC61869, IEEE C57.13
d. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
e. | Rated Primary Current | [5 empty] | 2000 for 5P20 ; 600/1200 for 0.2S | [12 empty] | A
f. | Rated Secondary Current | [5 empty] | 1 | [12 empty] | A
g. | No of core | [5 empty] | 4 for 5P20 ; 2 for 0.2S
h. | Current ratio | [5 empty] | 300/400/500/800/1,100/1,200/1,500/1,600/2,000 : 1//1//1//1 for 5P20 600 × 1,200 : 1//1 * for 0.2S
i. | Accuracy class | [5 empty] | 5P20, 20 VA and 0.2S, 20 VA
j. | Continuous thermal current rating factor | [5 empty] | 1
Surge Arrester
a. | Manufacturer/ Country | [5 empty] | N/A
b. | Type / Model / Catalog No. | [5 empty] | N/A
c. | Applied standard | [5 empty] | N/A
d. | Maximum service voltage | [5 empty] | N/A | [12 empty] | kV
e. | Class | [5 empty] | N/A
f. | Duty cycle current | [5 empty] | N/A | [12 empty] | kA
g. | Arrester insulation withstand, BIL | [5 empty] | N/A | [12 empty] | kV
h. | Maximum continuous operating voltage (Uc) | [5 empty] | N/A | [12 empty] | kV
i. | Maximum equivalent front-of-wave protective level | [5 empty] | N/A | [12 empty] | kV
j. | Maximum discharge voltage at 5/10/20 kA | [5 empty] | N/A | [12 empty] | kV
k. | Net weight of each arrester | [5 empty] | N/A | [12 empty] | kg
Bushing
a. | Manufacturer/ Country | [5 empty] | Xi'an XD, China
b. | Type / Model / Catalog No. | [5 empty] | ELK-04
c. | Applied standard | [5 empty] | IEC60137
d. | Maximum service voltage | [5 empty] | 145 | [12 empty] | kV
e. | Type of internal insulation | [5 empty] | SF6
f. | Type of external insulation | [5 empty] | Porcelain
g. | Nominal specific creepage distance | [5 empty] | 31 | [12 empty] | mm/kV
h. | Cantilever load | [5 empty] | 5000 | [12 empty] | N
i. | Type of line termination | [5 empty] | Terminal and terminal connector suitable for 2x1272 MCM ACSR (supplied by contractor)
SF6 Service and Storage Unit
a. Type | [6 empty] | N/A
b. Compression pressure | [6 empty] | N/A | [12 empty] | bar
c. Suction rate | [6 empty] | N/A | [12 empty] | m3/hr.
d. SF6 gas recovery down to | [6 empty] | N/A | [12 empty] | mbar
e. Vacuum pump rate | [6 empty] | N/A | [12 empty] | m3/hr.
f. Final vacuum down to | [6 empty] | N/A | [12 empty] | mbar
SF6 gas filling cart
a. Vacuum pump rate | [6 empty] | ≥ 16 | [12 empty] | m3/hr.
b. Evacuate rate down to | [6 empty] | ≤ 1 | [12 empty] | mbar
c. The weighing scale
- Range | [6 empty] | 0-120 | [12 empty] | kg
- Accuracy | [6 empty] | ±20 | [12 empty] | g
d. Pressure reducer for SF6 | [6 empty] | 0-10 | [12 empty] | bar
Portable SF6 gas leak detector
a. Sensitivity | [6 empty] | N/A | [12 empty] | ppmv
b. Accuracy | [6 empty] | N/A | [10 empty] | % of full scale
c. Digit display | [7 empty] | Yes | [5 empty] | No
SF6 gas quality measuring device
a. | Moisture content
| - Range of DEW point | [5 empty] | N/A | [12 empty] | oC
| - Accuracy | [5 empty] | N/A | [12 empty] | oC
| - Pump back function | [6 empty] | Yes | [5 empty] | No
b. | SF6 content
| - Range | [5 empty] | N/A | [11 empty] | % volume
| - Accuracy | [5 empty] | N/A | [11 empty] | % volume
Gas decomposition tester
a. | SO2
| - Range | [5 empty] | N/A | [12 empty] | ppmv
| - Acuuracy | [5 empty] | N/A | [12 empty] | %

## PD-18.1_HITACHI (hidden)
Proposal Data | [6 empty] | PANEL ASSEMBLY FOR CONTROL AND PROTECTION SYSTEM
PD 18.1 (1/1)
PANEL ASSEMBLY FOR CONTROL AND PROTECTION SYSTEM | [8 empty] | BIDDER NAME _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ | BID NO. _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
Bidder name: | PWH (THAILAND) COMPANY LIMITED
Bid No: | RTS3-S-02
Manufacturer: | Hitachi Energy (Thailand) Limited
MANUFACTURER_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
No. | Specification Detail | Data | Format Type ที่ต้องให้ Bidder กรอก | Benmark | a. | Make and Country of Origin |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
a. | Country of Origin | Thailand | Text |  | b. | Engineering Work |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
[5 empty] | c. | Blank Panel Maker |  |  |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
b. | Engineering Work | Hitachi Energy (Thailand) Limited | Text |  | [ ] | I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER).
[5 empty] | d. | Applied Standards
c. | Blank Panel Maker | Hitachi Energy (Thailand) Limited / Thailand | Text |  |  |  | Dielectric withstand | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
|  | [ X ] I certify that the manufacturers specified above are in accordance with the EGAT ACCEPTED MANUFACTURER LIST FOR CONTROL AND PROTECTION PANEL (LOCAL MANUFACTURER). |  |  |  |  | Insulation Resistance | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
d. | Applied Standards | [5 empty] | Temperature Range | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Dielectric withstand | 2000 Vac for 1 s | Digit |  | e. | Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - Insulation Resistance | 500 Vdc for 1 s | Digit |  | f. | The thickness of leveled sheet steel and | [ ] Yes | [ ] No
| - Temperature Range [°C] | 0 - 55 °C | Digit |  |  | formed steel members is not less than 2.5 mm. |  | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
e. | Type | Indoor Type | Text |  |  | If no, specify the supporting structure method. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
f. | The thickness of leveled sheet steel and | [ X ] Yes [ ] No | Yes No |  | g. | Degree of protection | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| formed steel members is not less than 2.5 mm. |  |  |  | h. | Ambient temperature | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ °C
| If no, specify the supporting structure method. |  | Text |  | i. | Ambient humidity | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ %
g. | Degree of protection | IP40 | Text |  | j. | Terminal Block
h. | Ambient temperature [°C] | 0 - 55 °C | Digit |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
i. | Ambient humidity [%] | 95% | Digit |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
j. | Other equipments [Type / Manufacturer] |  |  |  | k. | Miniature Circuit Breaker
| j1. Test switch |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Control and Protection | / | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For Metering | CMC252, F2100, RTS21 / OMICRON, DOUBLE, FREJA | Text
| j2. Undervoltage Relay | / | Text |  | l. | Switchboard wire
| j3. Terminal Block |  |  |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For AC/DC power supply | AVK, WGO, ASK Series/ Klemsan | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| - For PT and control circuits | AVK, WGO, ASK Series/ Klemsan | Text
| - For CT circuits | AVK, WGO, ASK Series/ Klemsan | Text |  | m. | Test Equipment
| - For Alarm/Status circuits and marshalling cabinet | AVK, WGO, ASK Series/ Klemsan | Text |  |  | - Manufacturer | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j4. Miniature Circuit Breaker | S200 Seires / ABB | Text |  |  | - Type | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| j5. Switchboard wire | PVC 600V / Local | Text
[5 empty] | n. | The normal size of drawings. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
k. | Specify type and manufacturer of spectial tool, |  | Text |  |  | If not A1, give reason. | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
| if needed. |  | Text |  | o. | Specify type and manufacturer of spectial tool, | _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
**Please fill in blue cell

## PD-29 (1.2)_HITACHI (hidden)
Proposal Data
PD 29 (1/2)
COMPUTER SET
Bidder name: | PWH (THAILAND) COMPANY LIMITED
Bid No: | RTS3-S-02
No. | Specification Detail |  |  | Data |  |  |  |  | Benmark
a. | Computer Set for HMI server
a1. Workstation
| - Quantity |  |  | 2 units
| - Main Processor Performance |  |  | Intel Core i7-10700
| - Memory (RAM) |  |  | 64GB DDR4 ECC
| - Storage |  |  | SSD 1TB M.22280
| - Number of Network Ports |  |  | 4 RJ45, 4 USB-C, 1 USB-A, 4 HDMI
| - Computer Operating System |  |  | Windows 11 Pro 64 bits
| - Power Supply |  |  | 600W
a2. Inverter Power Supply (if any)
- Model Type/Manufacturer
- Rated Power
- Voltage Input
- Voltage Output
a3. Display Monitor
| - Model Type/Manufacturer |  |  | P2425H / Dell
| - Quantity |  |  | 4 units
| - Size |  |  | 24"
| - Resolution |  |  | 1920 x 1080 at 60 Hz
a4. Mouse
| - Model Type/Manufacturer |  |  | MS116 / Dell
| - Quantity |  |  | 2 units
a5. Keyboard
| - Model Type/Manufacturer |  |  | KB216 / Dell
| - Quantity |  |  | 2 units
a6. Speaker
| - Model Type/Manufacturer |  |  | PEBBLE / Creative
| - Quantity |  |  | 2 units
a7. List of Supervisory Software
| No. | Software | Version | Description | Minimum Requirement
[5 empty] | Operating System | CPU | RAM | Storage
| 1 | Anti Virus |  | Trellix Protect Standard | Win11 | 2 Core | 4GB | 4GB
| 2 | AutoCAD | 2024 | Autodesk AutoCAD Commercial | Win11 | 2 Core | 4GB | 4GB
| 3 | Acrobat |  | Adobe Acrobat Standard DC | Win11 | 1.5 GHz | 2GB | 5GB
| 4 | MSOffice | 2024 | Microsoft Office Home & Business 2024 | Win11 | 3.0 GHz | 16GB | 7GB
5
**Please fill in blue cell

## PD-29 (2.2)_HITACHI (hidden)
Proposal Data
PD 29 (2/2)
COMPUTER SET
Bidder name: | PWH (THAILAND) COMPANY LIMITED
Bid No: | RTS3-S-02
No. | Specification Detail |  |  | Data |  |  |  |  | Benmark
b. | Computer Set for Engineering Workstation
b1. Device properties
| - Main Processor Performance |  |  | Intel Core i7-10700
| - Memory (RAM) |  |  | 64GB DDR4 ECC
| - Storage |  |  | SSD 1TB M.22280
| - Number of Network Ports |  |  | 4 RJ45, 4 USB-C, 1 USB-A, 4 HDMI
| - Computer Operating System |  |  | Windows 11 Pro 64 bits
| - Power Supply |  |  | 600W
b2. Display Monitor
| - Model Type/Manufacturer |  |  | P2425H / Dell
| - Quantity |  |  | 1 Unit
| - Size |  |  | 24"
| - Resolution |  |  | 1920 x 1080 at 60 Hz
b3. Mouse
| - Model Type/Manufacturer |  |  | MS116 / Dell
| - Amount |  |  | 1 Unit
b4. Keyboard
| - Model Type/Manufacturer |  |  | MS116 / Dell
| - Quantity |  |  | 1 Unit
b5. List of Supervisory Software / System Configuration Software
| No. | Software | Version | Description | Minimum Requirement
[5 empty] | Operating System | CPU | RAM | Storage
| 1 | McAfee |  | Endpoint Threat | Win11 | 2 Core | 4GB | 4GB
| 2 | Office |  | Home & Business | Win11 | 3.0 GHz | 16GB | 7GB
| 3 | AutoCad |  | Commercial New single-user | Win11 | 2 Core | 4GB | 4GB
| 4 | Acrobat |  | Adobe Acrobat Standard DC | Win11 | 1.5 GHz | 2GB | 5GB
| 5 | PCM600 |  | Hitachi Protection and control IED manager | Win16 | 1.5 GHz | 8GB | 6GB
| 6 | Network work management tool |  | MxView-50 or Industrai HiVision | Win7 | 2 GHz | 8GB | 10GB
| 7 | Windows Server 2022 |  |  | Server2022 | 2 GHz | 4GB | 32GB
| 8 | Window server users CALs 5-pack |  |  | Server2022 | 2 GHz | 2GB | 5GB
| 9 | Window server remote desktop service, user 5-pack |  |  | Server2022 | 2 GHz | 2GB | 5GB
| 10 | HDD Storage back-up
| 11 | DIGSI 5 |  | SIEMENS Engineering Tools | Win16 | 1.5 GHz | 8GB | 6GB
| 12 | S1 Agile |  | GE Engineering Tools | Win16 | 1.5 GHz | 8GB | 6GB
**Please fill in blue cell

## DX-1AB2_Tirathai (hidden)
DISTRIBUTION TRANSFORMER
FORM PD 111,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  |  | RTS3-S-02 | SCHEDULE NO. |  |  |  | 1AB2: Distribution
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  |  |  | ITEM NO. |  |  | 1AB2-1
a. | Manufacturer / Country |  |  |  |  | Tirathai Public Co.,Ltd./Thailand
b. | Type |  |  |  |  | 3 Ph, Outdoor oil immersed distribution Tr.
c. | Applied Standards |  |  |  |  | IEEE C57.12, TIS 384
d. | Max. Continuous Rated Capacity |  |  |  |  | 500 | [7 empty] | kVA
e. | Rated Voltage |  | - HV / LV |  |  | 22 |  |  |  | 0.4 |  |  |  | kV
f. | Rated Current |  | - HV / LV |  |  | 13.1 |  |  |  | 721.7 |  |  |  | A
g. | Impedance Voltage at Rated Voltage,
| Current, Frequency and 75 °C |  |  |  |  | ≥ 6.0 | [7 empty] | %
h. | Basic Insulation Level (BIL) of Windings
|  |  | - HV Winding |  |  | 150 | [7 empty] | kV
|  |  | - LV Winding |  |  | 30 | [7 empty] | kV
|  |  | - Neutral |  |  | 30 | [7 empty] | kV
i. | Vector Group |  |  |  |  | Dyn1
j. | Polarity |  |  |  |  | Subtractive
k. | Off Load Tap Changer
|  |  | - Manufacturer / Country |  |  | Tirathai PLC. / Thailand
|  |  | - Type / Model No. |  |  | BIL 200kV, 63A
|  |  | - Tapping Range |  |  | ± 2.5, ± 5 |  |  | % on |  | HV |  |  | Side
l. | Exciting Current in % of Full Load Current
| at 110 % / 100% / 90% / 80% Rated Voltage |  |  |  |  | 8.98 |  | 0.86 |  | 0.31 |  |  | 0.21 | %
m. | Efficiency with 0.9 Lagging Pf. Load
| at 110 % / 100% / 50% Load |  |  |  |  | 98.57 |  |  | 98.66 |  |  | 99.03 |  | %
n. | Max. Short Circuit Current which the Transformer
shall be able to withstand
|  | Symmetrical |  | - HV / LV Winding |  | 0.13 |  |  |  | 12.03 |  |  |  | kA rms
|  | Asymmetrical |  | - HV / LV Winding |  | 0.28 |  |  |  | 27.05 |  |  |  | kA peak
o. | Temperature Rise
|  | - Average Winding / Hottest Spot |  |  |  | 55 |  |  |  | 65 |  |  |  | °C
|  | - Insulating Oil |  |  |  | 55 | [7 empty] | °C
p. | Insulating Material
|  | Winding Insulation Paper |  |  | - Manufacturer | Miki / Japan
[5 empty] | - Temp. Class | A (105° C)
|  | Other Insulating Material |  |  | - Manufacturer | Weidmann / Switzerland
[5 empty] | - Temp. Class | A (105° C)
q. | Internal Gas Pressure Withstanding of Tank |  |  |  |  | 0.7 | [7 empty] | kg/cm2
r. | Insulating Oil |  | - Type |  |  |  | Uninhibited |  |  | X |  | Inhibited
|  |  | - Manufacturer |  |  | Shell / Thailand
|  |  | - Manufacturer Type |  |  | Diala S4-ZX-I
|  |  | - Applied Standard |  |  | IEC60296
s. | Bushing |  |  |  |  | HV |  |  | LV |  |  | Neutral
|  |  | - Manufacturer |  |  | Modern ceramic/Thailand
|  |  | - Type (Condenser or Solid) |  |  | Solid |  |  | Solid |  |  | Solid
|  |  | - Model No. |  |  | 20NF100 |  |  | 1NF1000 |  |  | 1NF1000
|  |  | - BIL |  |  | 150 |  |  | 30 |  |  | 30 |  | kV
|  |  | - Power Freq. Withstand (Dry) |  |  | 60 |  |  | 10 |  |  | 10 |  | kV
|  |  | - Power Freq. Withstand (Wet) |  |  | 50 |  |  | 10 |  |  | 10 |  | kV
|  |  | - Rated Current |  |  | 100 |  |  | 1000 |  |  | 1000 |  | A
|  |  | - Creepage Distance |  |  | 455 |  |  | 75 |  |  | 75 |  | mm
t. | Cable Terminations
|  |  | - Manufacturer |  |  | -
|  |  | - Type / Model / Cat. No. |  |  | -
|  |  | - Material of External Insulator |  |  | -
|  |  | - Rated Voltage |  |  | - | [7 empty] | kV
|  |  | - Current Rating |  |  | - | [7 empty] | A
|  |  | - BIL |  |  | - | [7 empty] | kV
|  |  | - Aerial Conductor |  |  | -
|  |  | - Creepage Distance |  |  | - | [7 empty] | mm
|  |  | - Applied Standard |  |  | -
u. | Total Weight With Oil |  |  |  |  | Approx. 2600 | [7 empty] | kg
v. | Weight of Oil |  |  |  |  | Approx. 440 | [7 empty] | kg
w. | Volume of Oil |  |  |  |  | Approx. 490 | [7 empty] | Litres
x. | Overall Length ´ Width ´ Height |  |  |  |  | Approx 1.99 x 2.07 x 1.77 | [7 empty] | m × m × m
y. | Mounting |  |  |  |  | Platform
z. | Dimension of Base |  |  |  |  | 0.7 x 0.85 | [7 empty] | m × m
Guaranteed Characteristics
| - No-load Loss at Rated Voltage and Frequency |  |  |  |  | 900 | [7 empty] | W
| - Load Loss at Rated Capacity, Voltage and |  |  |  |  | 5200 | [7 empty] | W
Frequency at 75 °C
| - Total Loss at Rated Capacity, Voltage and |  |  |  |  | 6100 | [7 empty] | W
Frequency at 75 °C
Important Notice:
The guaranteed characteristics shall be evaluated and included in the bid price for cost evaluation with the rate of
190 baht for each W or part thereof of the guaranteed no-load loss.
69 baht for each W or part thereof of the guaranteed load loss.
If the transformer fail to meet the guaranteed characteristics herein indicated, the price of transformers shall be reduced in accordance with the condition specified in Article : Penalty for Equipment not Meeting Guaranteed Characteristics.

## SA-1AB4_Siemens Ene (hidden)
SURGE ARRESTER
FORM PD 392,393,394,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB4
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB4-1
a. | Manufacturer / Country
|  | - For SA |  | Siemens Energy/ Germnay
|  | - For Supporting Structure |  | SIAM STEEL TOWER CO.,LTD./ THAILAND
b. | Type / Model / Catalog No. |  |  | ZnO/3EP/3EP4 108-2PE31-1XA1-Z
c. | Applied Standards |  |  | IEEE C62.11
d. | Class (Station or Distribution) |  |  | Station Class
e. | Arrester Voltage Rating |  |  | 108 |  |  |  | kVrms
f. | Duty Cycle Current |  |  | 10 |  |  |  | kA
g. | Arrester Insulation Withstand
|  | - For BIL / 1 Min Dry / 10 s Wet |  | 658 | 337 |  | 267 | kV
h. | Rated Frequency |  |  | 50 |  |  |  | Hz
i. | Maximum Continuous Operating Voltage (MCOV) |  |  | 84 |  |  |  | kVrms
j. | Maximum Equivalent Front-of-wave |  |  | 277 |  |  |  | kVcrest
Protective Level
k. | Maximum Switching Surge Protective Level |  |  | 208 |  |  |  | kVcrest
l. | Maximum Discharge Voltage at 5/ 10 / 20 kA |  |  | 239 | 254 |  | 282 | kVcrest
m. | One Minute Energy Absorption Capability |  |  | 4,0 |  |  |  | kJ/kV
at Maximum L-G Voltage (45oC Ambient)
n. | Power Frequency Reference Voltage |  |  | 108,0…116,6 |  |  |  | kVrms
o. | Power Frequency Reference Current |  |  | 3,0 |  |  |  | mA peak/ cm2
p. | Leakage Current at
|  | - MCOV |  | ≤1,5 |  |  |  | mA
|  | - Nominal System L-G Voltage |  | ≤1,2 |  |  |  | mA
q. | RIV at 1.05 Max. System L-G Operating Voltage |  |  | ≤200 (PD Level ≤ 10 Pc |  |  |  | µV
r. | Creepage Distance of Insulator |  |  | 3405 |  |  |  | mm
s. | Insulator Color |  |  | Porcelain brown
t. | Weight |  |  | ~ 73 |  |  |  | kg
u. | Discharge Counter
|  | - Manufacturer / Country |  | Siemens Energy /China
|  | - Type / Model |  | Electromechanical /3EX5 050-0A
|  | - Minimum Impulse Registration |  | 200 |  |  |  | A
|  | - Registration Capability per Second |  | 5
|  | - Indicating Ammeter Scale |  | 0~10 |  |  |  | mA peak

## SA-1AB4_Hitachi (hidden)
SURGE ARRESTER
FORM PD 392,393,394,1001
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB4
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB4-1
a. | Manufacturer / Country
|  | - For SA |  | Hitachi Energy Sweden AB
|  | - For Supporting Structure |  | SIAM STEEL TOWER CO.,LTD./ THAILAND
b. | Type / Model / Catalog No. |  |  | EXLIM Q108-EH123
c. | Applied Standards |  |  | ANSI/IEEE C62.11
d. | Class (Station or Distribution) |  |  | Station
e. | Arrester Voltage Rating |  |  | 108 |  |  |  | kVrms
f. | Duty Cycle Current |  |  | 10 |  |  |  | kA
g. | Arrester Insulation Withstand
|  | - For BIL / 1 Min Dry / 10 s Wet |  | 550 | 280 |  | 230 | kV
h. | Rated Frequency |  |  | 50 |  |  |  | Hz
i. | Maximum Continuous Operating Voltage (MCOV) |  |  | 84 |  |  |  | kVrms
j. | Maximum Equivalent Front-of-wave |  |  | 275 at 10kA |  |  |  | kVcrest
Protective Level
k. | Maximum Switching Surge Protective Level |  |  | 208 at 0.5kA & 214 at 1kA |  |  |  | kVcrest
l. | Maximum Discharge Voltage at 5/ 10 / 20 kA |  |  | 242 | 254 |  | 280 | kVcrest
m. | One Minute Energy Absorption Capability |  |  | 9 kJ/kV MCOV |  |  |  | kJ/kV
at Maximum L-G Voltage (45oC Ambient)
n. | Power Frequency Reference Voltage |  |  | ≥108 |  |  |  | kVrms
o. | Power Frequency Reference Current |  |  | 0.07 |  |  |  | mA peak/ cm2
p. | Leakage Current at
|  | - MCOV |  | <1,5 (Nominal) |  |  |  | mA
|  | - Nominal System L-G Voltage |  | <1,5 (Nominal) |  |  |  | mA
q. | RIV at 1.05 Max. System L-G Operating Voltage |  |  | < 200 |  |  |  | µV
r. | Creepage Distance of Insulator |  |  | 3685 |  |  |  | mm
s. | Insulator Color |  |  | Brown, Porcelain
t. | Weight |  |  | Approx 88 |  |  |  | kg
u. | Discharge Counter
|  | - Manufacturer / Country |  | TE Connectivity / Germany
|  | - Type / Model |  | SC13
|  | - Minimum Impulse Registration |  | 2++ |  |  |  | A
|  | - Registration Capability per Second |  | 5
|  | - Indicating Ammeter Scale |  | 0-30 |  |  |  | mA peak

## PF-1AB11_S&C (hidden)
POWER FUSE AND HOOK STICK
FORM PD 251
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB11, 1D11
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  |  | ITEM NO. | 1AB11-1, 1AB11-2, 1D11-1 and 1D11-2
a. | Make and Country of Origin |  |  |  | S&C ELECTRIC CO., LTD, U.S.A.
b. | Type/Model/Cat.No |  |  |  | SMD-40 Cat. 192323-SP-LLB
c. | Applied Standards |  |  |  | ANSI C37.46
d. | Rated Maximum Voltage |  |  |  | 29 |  |  | kV
e. | Frequency |  |  |  | 50 |  |  | Hz
f. | Insulator Level
Power Frequency Withstand (Dry), rms
| Terminal-to-Terminal |  |  |  | 77 |  |  | kV
Impulse Withstand (BIL), Peak
| Terminal-to-Terminal |  |  |  | 165 |  |  | kV
g. | Current Rating |  |  |  | 400 |  |  | A
h. | Rated Interrupting rms Symmetrical Current |  |  |  | 16 |  |  | kA
i. | Mounting Position |  |  |  | STATION-VERTICAL
j. | Insulator
| - Make/Type |  |  |  | SUZHOU CHINA/STATION POST (GREY)
| - Manufacturer Reference No |  |  |  | 347310E2
| - NEMA Technical Reference No |  |  |  | TR210
| - Impulse Withstand (BIL) |  |  |  | 200 |  |  | kV
| - Creepage Distance |  |  |  | 950 |  |  | mm
- Mechanical Strength
|  | - Cantilever |  |  | 907.3 |  |  | kg
|  | - Tension |  |  | 5442.17 |  |  | kg
|  | - Mounting Bolt Circle |  |  | 7.6 |  |  | cm
k. | Rated Continuous Current of Fuse Link or Refill Unit
| - Item No. |  | 1AB11-2 |  | 20 | A,Cat.No | 823020
| - Item No. |  | 1D11-1 |  | 20 | A,Cat.No | 823020
| - Item No. |  |  |  |  | A,Cat.No
| - Item No. |  |  |  |  | A,Cat.No
l. | Weight per Phase |  |  |  | 60 Kg
m. | Make and Country of Origin of Hook Stick |  |  |  | S&C/USA

## LCUS-1AB12-1_Precise Ele (hidden)
LOAD CENTER UNIT SUBSTATION (LCUS)
FORM PD 434
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  |  | 1AB12
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. |  | 1AB12-1
a. | Make and Country of Origin |  |  | Precise / Thailand
b. | Type |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Circuit Voltage |  |  | 400 | [6 empty] | V
e. | Frequency |  |  | 50 | [6 empty] | Hz
f. | Main Bus Current Rating |  |  | 1000 |  | A |  | 1.55 |  | A/mm2
g. | Main Circuit Breaker
| - Make and Country of Origin |  |  | LS / Korea
| - Type/Model/Cat.No |  |  | AN-D
- Voltage Rating
| - Rated |  |  | 690 | [6 empty] | V
| - Maximum |  |  | 1000 | [6 empty] | V
- Current Rating
| - Continuous |  |  | 400~1000 | [6 empty] | A
| - Interrupting |  |  | 65 | [6 empty] | kA
| - Thermal Setting Range |  |  | 400~1000 | [6 empty] | A
| - Magnetic Setting Range |  |  | 600~1000 | [6 empty] | A
| - Control Circuit Voltage |  |  | 125 | [6 empty] | Vdc
| - Motor Supply Voltage |  |  | 125 | [6 empty] | Vdc
h. | Branch Circuit Breaker
| - Make and Country of Origin |  |  | LS / Korea
| - Type/Model/Cat.No |  |  | TS250N |  | TS250N |  |  | TS250N
| - Voltage Rating |  |  | 690 |  | 690 |  |  | 690 |  | V
| - Frame Rating |  |  | 250 |  | 250 |  |  | 250 |  | A
| - Trip Rating |  |  | 125, 160 |  | 200 |  |  | 250 |  | A
| - Interrupting Rating |  |  | 42/480 |  | 42/480 |  |  | 42/480 |  | kA/V
| - Magnetic Trip Adjustable |  |  | X | Yes | X | Yes |  | X | Yes
[5 empty] | No |  | No |  |  | No
i. | Current Transformer
| - Make and Country of Origin |  |  | Precise / Thailand
| - Accuracy Class |  |  | 0.5 | [6 empty] | VA
| - Burden |  |  | 15 | [6 empty] | D
| - Current Ratio |  |  | 800/5
k. | Energy Meter
| - Make Country of Origin |  |  | ISKRA / Slovania
| - Type |  |  | MC740
l. | Indicating Meter
| - Make Country of Origin |  |  | ISKRA / Slovania
| - Type |  |  | CQ2207
m. | Relay
| - Make Country of Origin |  |  | TELE/Austria
| - Type |  |  | G2PM400VSY20
n. | Dimension of LCUS Board (HxWxD) |  |  | H2300 x W2400 x D(800+251+202) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 | [6 empty] | mm
p. | Total Weight |  |  | 1000 | [6 empty] | kg

## ORB rev.1-1AB12-4_Precise Ele (hidden)
COMMON CUBICLE AND OUTDOOR RECEPTACLE BOX
FORM PD ORB
Apr. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB12
BIDDER |  | PWH (THAILAND) CO., LTD. |  | ITEM NO. | 1AB12-4
a. | Make and Country of Origin |  |  | Precise / Thailand
b. | Type / Model No |  |  | Outdoor Type
c. | Applied Standards |  |  | IEC
d. | Cross-section Dimension of bus
| - Neutral Bus |  |  | 30x5 (232.5 A , 1.55A/mm2) |  |  |  | mm*mm
| - Ground Bus |  |  | 30x5 (232.5 A , 1.55A/mm2) |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  | V
f. | 3-Pole Main Breaker
| - Make/Type |  |  | ABB/Tmax XT2N
| - Trip Rating/Max Voltage |  |  | 64~160 / 415 |  |  |  | A/V
| - Frame Rating |  |  | 160 |  |  |  | A
| - Interrupting Rating |  |  | 36 |  |  |  | kA
g. | Earth Leakage Circuit Breaker
| - Make/Type |  |  | SCHNEIDER/iC60H
| - Trip Rating/Max Voltage |  |  | 20/240 |  |  |  | A/V
| - Frame Rating |  |  | - |  |  |  | A
| - Interrupting Rating |  |  | 10 |  |  |  | kA
| - Sensitivity |  |  | 30 |  |  |  | mA
h. | Terminal Block
| - Manufacturer / Country |  |  | TOGI/Japan
| - Type / Model / Catalogue No. |  |  | PT-150
| - Rating |  |  | 1000 | V/ | 175 |  | A
- Material
| - Short-Circuit Type |  |  |  | Yes | X | No
| - Suitable for Cable |  |  | 95-175 |  |  |  | mm2
i. | Power Receptacle
| - Make/Type |  |  | AST/Power Plug
| - No of Phase/No of Wire |  |  | 3 Phase / 5 Wire
| - Rated Current/Voltage |  |  | 32 / 400 |  |  |  | A/V
j. | Receptacle
| - Make/Type |  |  | PANASONIC
| - Rated Current/Voltage |  |  | 15/250 |  |  |  | A/V
k. | Outdoor Receptacle Box Dimensions
| - CCM type 1 | [6 empty] | mm×mm×mm
| - CCM type 2 | [6 empty] | mm×mm×mm
| - ORB1 | [6 empty] | mm×mm×mm
| - ORB2 | [6 empty] | mm×mm×mm
| - ORB3 |  |  | W(800+50+50) x D(200+100) x H1080 |  |  |  | mm×mm×mm
l. | Sheet Steel Thickness
| - CCM type 1 | [6 empty] | mm
| - CCM type 2 | [6 empty] | mm
| - ORB1 | [6 empty] | mm
| - ORB2 | [6 empty] | mm
| - ORB3 |  |  | 2.5 |  |  |  | mm
m. | Total Weight
| - CCM type 1 | [6 empty] | kg
| - CCM type 2 | [6 empty] | kg
| - ORB1 | [6 empty] | kg
| - ORB2 | [6 empty] | kg
| - ORB3 |  |  | 100 |  |  |  | kg

## LBS-1AB12-5_Precise Ele (hidden)
LOAD BREAK SWITCH AND FUSE
FORM PD LBSW
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB12
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. |  | 1AB12-5
Panel Assembly Manufacturer / Country |  |  |  | Precise / Thailand
A. LOAD BREAK SWITCH
a. | Make and Country of Origin |  |  | ABB / Poland
b. | Type/Model/Cat. No |  |  | NAL
c. | Applied Standards |  |  | IEC
d. | Rated Voltage |  |  | 24 |  |  |  |  | kV
e. | Maximum Service Voltage |  |  | 24 |  |  |  |  | kV
f. | Basic Impulse Voltage |  |  | 125 |  |  |  |  | kV
g. | Current Rating
- Main Switch
|  | - Rated normal current |  | 630 |  |  |  |  | A
|  | - Rated short time withstand current (1 s) |  | 25 |  |  |  |  | kA
|  | - Rated peak withstand current |  | 82 |  |  |  |  | kA
- Grounding Switch
|  | - Rated short time withstand current |  | 25 |  |  |  |  | kA
|  | - Rated peak withstand current |  | 82 |  |  |  |  | kA
h. | Phase Spacing |  |  | 275 |  |  |  |  | mm
i. | Tripping Device Actuated by Striker Pin |  |  |  |  | Yes | X | No
j. | Number of Auxiliary Switch |  |  | 2 NO + 2NC
k. | Have confined arc quenching chamber for |  |  |  | X | Yes |  | No
air blow arc quenching
B. POWER FUSE
aa. | Make and Country of Origin |  |  | -
bb. | Type/Model/Cat. No |  |  | -
cc. | Applied Standards |  |  | -
dd. | Rated Voltage |  |  | - |  |  |  |  | kV
ee. | Maximum Service Voltage |  |  | - |  |  |  |  | kV
ff. | Basic Impulse Voltage |  |  | - |  |  |  |  | kV
gg. | Fuse Element Current Rating |  |  | - |  |  |  |  | A
hh. | Max Interrupting Rating |  |  | - |  |  |  |  | kA
ii. | Power Fuse Support Current Rating |  |  | - |  |  |  |  | kA
jj. | Fuse Blow Striker Pin Actuator |  |  |  |  | Yes |  | No

## DB-AB12-6_Precise Ele (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB12
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB12-6
a. | Make and Country of Origin |  |  | Precise / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 465 (1.55A/mm2) |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 9.52 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | LS / ABN101d
| - Trip Rating/Max Voltage |  |  | / | 32/415 |  | / |  | A/V
| - Frame Rating |  |  |  | 100 |  |  |  | A
| - Interrupting Rating |  |  |  | 25 |  |  |  | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABS103c, TS100N, TS160N
| - Trip Rating/Max Voltage |  |  | 30,75/690 | 80~100/690 |  | 128~160/690 |  | A/V
| - Frame Rating |  |  | 125 | 100 |  | 160 |  | A
| - Interrupting Rating |  |  | 37 | 50 |  | 50 |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / TS400N
| - Trip Rating/Max Voltage |  |  | / | 160~400 / 690 |  | / |  | A/V
| - Frame Rating |  |  |  | 400 |  |  |  | A
| - Interrupting Rating |  |  |  | 65 |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | Precise /LDB-35
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 12.5 |  |  |  |  | VA
| - Ratio |  |  | 400/5
n. | Distribution Board dimension (HxWxD) |  |  | H2250 x W800 x D(500+251+202) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## DB-AB12-7_Precise Ele (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB12
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB12-7
a. | Make and Country of Origin |  |  | Precise / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 (1.55A/mm2) |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 400/230 |  |  |  |  | V
f. | 1-Pole Branch Breaker
- Make/Type
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
h. | 3-Pole Branch Breaker
| - Make/Type |  |  | LS / ABS103c
| - Trip Rating/Max Voltage |  |  | 30/690 | 100/690 |  | / |  | A/V
| - Frame Rating |  |  | 125 | 125 |  |  |  | A
| - Interrupting Rating |  |  | 37 | 37 |  |  |  | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | LS / TS250N
| - Trip Rating/Max Voltage |  |  |  | 100~250 / 690 |  | / |  | A/V
| - Frame Rating |  |  |  | 250 |  |  |  | A
| - Interrupting Rating |  |  |  | 42 |  |  |  | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
| - Make/Type |  |  | Precise /LDB-35
| - Accuracy Class |  |  | 0.5
| - Burden |  |  | 12.5 |  |  |  |  | VA
| - Ratio |  |  | 250/5
n. | Distribution Board dimension (HxWxD) |  |  | H2250 x W800 x D(500+251+202) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## 125PANEL-AB12-8_Precise Ele (hidden)
125 Vdc POWER PANEL
FORM PD 430.1
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB12
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB12-8
a. | Make and Country of Origin |  |  | Precise / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 1000 (1.55A/mm2) |  |  | A
| - Cross-section Dimension of bus |  |  | 50.8 x 12.7 |  |  | mm*mm
e. | Rated Voltage |  |  | 125
f. | 2-Pole Molded Case Switch
| - Make/Type |  |  | SIEMENS / 3KD38, SIEMENS / 3KD46
| - Current Rating/Max Voltage |  |  | 250 / 440 | 630 / 440 |  | A/Vdc
| - Frame Rating |  |  | 250, 630 |  |  | A
g. | 2-Pole Molded Case Breaker
| - Make/Type |  |  | MITSUBISHI / NF250-SV
| - Trip Rating/Max Voltage |  |  | 630 / 250 |  |  | A/Vdc
| - Frame Rating |  |  | 630 |  |  | A
| - Interrupting Rating |  |  | 50 |  |  | kA
h. | Ammeter
| - Make/Type |  |  | ISKRA/BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  | degree
I. | Voltmeter (0-150 Vdc)
| - Make/Type |  |  | ISKRA/BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  | degree
j. | Voltmeter (150-0-150 Vdc)
| - Make/Type |  |  | ISKRA/BQ2207
| - Accuracy (% of full scale) |  |  | 1 |  |  | %
| - Full Scale Deflection Angle |  |  | 240 |  |  | degree
k. | Volmeter Selector Switch (VS)
| - Make/Type |  |  | K&N/CA10
| - Voltage Rating |  |  | 600 |  |  | V
| - Current Rating |  |  | 20 |  |  | A
l. | Under Voltage Relay (27)
| - Make/Type |  |  | TELE / G2UM300VL20
| - Adjustable Voltage Range |  |  | 15~285Vdc |  |  | V
| - Current Rating of Contact |  |  | 5 |  |  | A
m. | Ground Detector
| - Make/Type |  |  | WISCO/IR195
| - Current Rating of Contact |  |  | 3A at 125 Vac |  |  | A
n. | Distribution Board Dimensions |  |  | H2500 x W800 x D(500+251+202) |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  | mm
p. | Total Weight |  |  | 400 |  |  | kg

## DB-AB12-9_Precise Ele (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB12
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB12-9
a. | Make and Country of Origin |  |  | Precise / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 (1.55A/mm2) |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | LS / ABS102c
| - Trip Rating/Max Voltage |  |  | 30/500 | 50/500 |  |  |  | A/Vdc
| - Frame Rating |  |  | 125 | 125 |  |  |  | A
| - Interrupting Rating |  |  | 20 | 20 |  |  |  | kA
h. | 3-Pole Branch Breaker
- Make/Type
| - Trip Rating/Max Voltage | [7 empty] | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
- Make/Type
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | H2500 x W800 x D(500+251+202) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## DB-AB12-10_Precise Ele (hidden)
AC & DC DISTRIBUTION BOARD
FORM PD 430
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB12
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB12-10
a. | Make and Country of Origin |  |  | Precise / Thailand
b. | Type /Model No |  |  | Enclosed Type
c. | Applied Standards |  |  | IEC
d. | Main Bus
| - Rated Bus Capacity |  |  | 312 (1.55A/mm2) |  |  |  |  | A
| - Cross-section Dimension of Bus |  |  | 31.75 x 6.35 |  |  |  |  | mm*mm
e. | Rated Voltage |  |  | 125 |  |  |  |  | V
f. | 1-Pole Branch Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
g. | 2-Pole Branch Breaker
| - Make/Type |  |  | LS / ABS102c
| - Trip Rating/Max Voltage |  |  |  | 50/500 |  |  |  | A/Vdc
| - Frame Rating |  |  |  | 125 |  |  |  | A
| - Interrupting Rating |  |  |  | 20 |  |  |  | kA
h. | 3-Pole Branch Breaker
- Make/Type
| - Trip Rating/Max Voltage | [7 empty] | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
i. | 2-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/Vdc
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
j. | 3-Pole Main Breaker
| - Make/Type |  |  | /
| - Trip Rating/Max Voltage |  |  | / | / |  | / |  | A/V
| - Frame Rating | [7 empty] | A
| - Interrupting Rating | [7 empty] | kA
k. | Kilowatthour Meter
| - Make/Type |  |  | /
| - No of Phase/No of Wire/Freq. |  |  | / | / |  | 50 Hz
| - Integration Period of the Maximum | [7 empty] | min
Demand Meter
| - Maximum Demand Indicator Scale | [7 empty] | kW
l. | 64B Ground Detector Relay
- Make
- Type
m. | Current Transformer
- Make/Type
- Accuracy Class
| - Burden | [7 empty] | VA
- Ratio
n. | Distribution Board dimension (HxWxD) |  |  | H2500 x W800 x D(500+251+202) |  |  |  |  | mm*mm*mm
o. | Sheet Steel Thickness |  |  | 2.5 |  |  |  |  | mm
p. | Total Weight |  |  | 400 |  |  |  |  | kg

## BATT-1AB13-1_GPT (hidden)
VENTED STATIONARY BATTERY AND BATTERY CHARGER
FORM PD AB 13
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB13
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB13-1
VENTED STATIONARY BATTERY
a. | Manufacturer / Country
| - Battery |  |  | Enersys / Poland
| - Battery Rack |  |  | Glow Power Technology / THAILAND
| - Electrolyte |  |  | KGHM/Poland,Gower Chemical/UK
(Bidder shall submit the certificate issued
by battery manufacturer to certify that the
proposed electrolyte is compatible with the battery.)
b. | Type / Model No. / No. of Cell |  |  | LEAD ACID / 19OPzS 2375 / 58 Cells
c. | Applied Standards |  |  | DIN Standard 40736-1 / IEC 896-11
BATTERY CHARGER
a. | Manufacturer / Country
b. | Type / Model No.
c. | Applied Standards
Note :
- Certification of country of origin, production’s lot no. and manufacturing date of the battery certified by
Chamber of Commerce shall be submitted along with the Equipment at the time of shipment.
- The contractor shall provide the rating capacity of the battery and the charger as design calculation approved by EGAT
but not less than the proposed capacity as specified in this proposal without the change of the contract price.

## BATT-1AB13-2_GPT (hidden)
VENTED STATIONARY BATTERY AND BATTERY CHARGER
FORM PD AB 13
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB13
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB13-2
VENTED STATIONARY BATTERY
a. | Manufacturer / Country
- Battery
- Battery Rack
- Electrolyte
(Bidder shall submit the certificate issued
by battery manufacturer to certify that the
proposed electrolyte is compatible with the battery.)
b. | Type / Model No. / No. of Cell
c. | Applied Standards
BATTERY CHARGER
a. | Manufacturer / Country |  |  | BIRA BROTHERS CO.,LTD./THAILAND
b. | Type / Model No. |  |  | SCR full wave rectifier / 150CG - 400
c. | Applied Standards |  |  | NEMA PE5-1997 (R2003)
Note :
- Certification of country of origin, production’s lot no. and manufacturing date of the battery certified by
Chamber of Commerce shall be submitted along with the Equipment at the time of shipment.
- The contractor shall provide the rating capacity of the battery and the charger as design calculation approved by EGAT
but not less than the proposed capacity as specified in this proposal without the change of the contract price.

## BATT_4G (hidden)
VENTED STATIONARY BATTERY AND BATTERY CHARGER
FORM PD AB 13
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB13
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. |  | 1AB13
*-
VENTED STATIONARY BATTERY
a. | Manufacturer / Country
| - Battery |  |  | EXIDE TECHNOLOGIES / FRANCE
| - Battery Rack |  |  | 4G ENGINEERING / THAILAND
| - Electrolyte |  |  | LEE CIER HUAD / THAILAND
(Bidder shall submit the certificate issued
by battery manufacturer to certify that the
proposed electrolyte is compatible with the battery.)
b. | Type / Model No. / No. of Cell |  |  | Vented lead / 22 OPzS 2750 LA / 58
c. | Applied Standards |  |  | Din 40736
BATTERY CHARGER
a. | Manufacturer / Country |  |  | 4G ENGINEERING / THAILAND
b. | Type / Model No. |  |  | Thyristor controlled / LFB3-130-500(450A)
c. | Applied Standards |  |  | NEMA-PE5
Note :
- Certification of country of origin, production’s lot no. and manufacturing date of the battery certified by
Chamber of Commerce shall be submitted along with the Equipment at the time of shipment. |  |  |  |  | *-+
- The contractor shall provide the rating capacity of the battery and the charger as design calculation approved by EGAT
but not less than the proposed capacity as specified in this proposal without the change of the contract price.

## FM-POW-P02_4G (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [6 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  | PROCUREMENT REFERENCE : RTS3-S-02 |  |  |  |  | Text
48 VDC VENTED STATIONARY LEAD-ACID BATTERY |  | SCHEDULE NO. : 1AB34 |  |  |  |  | Text
|  | ITEM NO. : 1AB34 |  |  |  |  | Text
|  | BIDDER : |  | PWH (THAILAND) COMPANY LIMITED |  |  | Text
1. | Make and Country of Origin | EXIDE TECHNOLOGIES / FRANCE |  |  |  |  | Text
2. | Model | 8 OPzS 800 LA |  |  |  |  | Text
3. | Capacity at 10 hr. rated 1.80 VPC. 25o C | 937 |  |  |  | Ah | Digit
4. | Type
| - Vented Stationary Lead-Acid type |  | [x] | Yes | [ ] No |  | Yes No
5. | Codes and standards |  | [ ] | IEEE | [ ] ASTM |  | Select
|  |  | [ ] | IEC | [ ] NEMA
|  |  | [ ] | ANSI | [ ] DIN
|  |  | [ ] | ASME | [ ] JIS
|  |  | [x] | IEC 60896-1
6. | Battery Configuration
| - Number of cell per set | 24 |  |  |  | Cell | Digit
Technical requirement for Battery (24 cells)
1. | Nominal voltage | 48 |  |  |  | V | Digit
2. | Current capacity | 937 |  |  |  | Ah | Digit
3. | Discharge characteristic | 43.2V of final voltage based on a 10 hour discharge rate |  |  |  |  | Digit
4. | Battery life at 20 Co | 20 |  |  |  | years | Digit
5. | Manufacturing age | No longer than 3 months since the manufacturing date |  |  |  |  | Digit
6. | Temperature | 0-40 |  |  |  | C° | Digit
7. | Relative humidity | 0-95 |  |  |  | % | Digit
8. | Self-discharge rate (per month) | 0.083 |  |  |  | % | Digit
Technical requirement for Cell
1. | Volt per cell | 2 |  |  |  | V | Digit
2. | Discharge characteristic | Final voltage of 1.8 V based on an 10 hours discharge rate |  |  |  |  | Digit
3. | Component
| - Positive plate shall be Tubular type |  | [x] | Yes | [ ] No |  | Yes No
| - Negative plate shall be Pasted/Flat type |  | [x] | Yes | [ ] No |  | Yes No
| - Lead antimony plate |  | [x] | Yes | [ ] No |  | Yes No
4. | Container and cover
| - The container and cover of each cell shall be made of ABS. |  | [x] | Yes | [ ] No |  | Yes No
| - Container and cover shall have inherent acid-resisting, |  | [x] | Yes | [ ] No |  | Yes No
shock-absorbing, heat-resisting , acid leak-proof qualification.
5. | Electrolyte
| - A dilute translucent sulfuric acid shall be used as an electrolyte. The substance shall conform to the ITSI standard and it shall be free from organic, iron, platinum and other impurities that may be harmful to the battery life. |  | [x] | Yes | [ ] No |  | Yes No
| - The specific gravity |  |  | 1.24 kg/L
| - 10% of the total volume of tropical electrolyte provided in the contract shall be spared as an extra and it shall, as well, conform to the ITSI standard. |  | [x] | Yes | [ ] No |  | Yes No
| - The containers of electrolyte provided for EGAT shall be newly made and they shall conform to the ITSI standard. |  | [x] | Yes | [ ] No |  | Yes No
6. | Connector
| - Shall be flexible lead or copper material with insulation sheath covered. |  | [x] | Yes | [ ] No |  | Yes No
7. | Bolts, nuts and washers
| - Made of metal with acid-resisting and rust-free qualification. |  | [x] | Yes | [ ] No |  | Yes No
8. | Bus cover and terminal
| - Shall be electrical insulator. |  | [x] | Yes | [ ] No |  | Yes No
9. | Cell numbering label
| - The running cell numbering label shall be specified |  | [x] | Yes | [ ] No |  | Yes No
in sequence, i.e. 1, 2, 3 … 24.
10. | Spare accessories
Shall be required to supply extra accessories as follows
| - 4 sets of inter-cell connector and 1 set of inter-step connector |  | [x] | Yes | [ ] No |  | Yes No
| - 2 sets of bolts, nuts and washers |  | [x] | Yes | [ ] No |  | Yes No
| - 2 sets of bus cover and terminal. |  | [x] | Yes | [ ] No |  | Yes No
Technical requirement for battery rack
1. | Rack structure
| - Shall be made of steel material with 2-step structure. |  | [x] | Yes | [ ] No |  | Yes No
| - The rail of each row shall be covered with hard rubber |  | [x] | Yes | [ ] No |  | Yes No
sheet in order to prevent any damages on the battery cell.
2. | Color
| - Shall be painted with acid resistant gray color RAL7036 |  | [x] | Yes | [ ] No |  | Yes No
with double coating procedure.
Accessories and maintenance tools
1. | Rod type thermometer | 3 |  |  |  | sets | Digit
2. | Syringe type hydrometer | 3 |  |  |  | sets | Digit
3. | Acid jug | 1 |  |  |  | each | Digit
4. | Filling funnel | 1 |  |  |  | each | Digit
5. | Non-oxide grease | 1 |  |  |  | can | Digit
6. | Filling syringe | 1 |  |  |  | each | Digit
7. | Acid-resistance glove | 2 |  |  |  | pairs | Digit
8. | Installation, Operation and Maintenance Manual | 1 |  |  |  | set | Digit
9. | AC/DC Clamp Meter | 1 |  |  |  | set | Digit
10. | Maintenance tool box to accommodate the above accessories | 2 |  |  |  | boxes | Digit
Other
1. | Float charging voltage applied per cell | 2.23 |  |  |  | V | Digit
2. | Equalize charging voltage applied per cell | 2.33 |  |  |  | V | Digit
3. | Battery cells :
| - Dimension | ____212____L____193____W____686____H |  |  |  | mm | Digit
| - Weight | 59.9 |  |  |  | kg | Digit
4. | Battery rack :
| - Dimension | ___2800___L____600____W____800____H |  |  |  | mm | Digit
| - Weight | 100 |  |  |  | kg | Digit
| - Arrangement of modules equipped in a rack | _______1_______Row_______2_______Tier |  |  |  |  | Digit
| - Floor loading | 915 |  |  |  | kg/sq.mm | Digit

## FM-POW-P03_4G (hidden)
PLEASE FILL OUT AND RETURN WITH YOUR PROPOSAL | [5 empty] | Format Type ที่ต้องให้ Bidder กรอก | Benmark
|  | PROCUREMENT REFERENCE : RTS3-S-02 |  |  |  | Text
48VDC CONVENTIONAL TYPE CHARGER |  | SCHEDULE NO. 1AB34 |  |  |  | Text
|  | ITEM NO. 1AB34 |  |  |  | Text
|  | BIDDER : |  | PWH (THAILAND) COMPANY LIMITED |  | Text
a. | Make and Country of Origin | EXZON \ THAILAND |  |  |  | Text
b. | Type | [X] | Constant voltage, Silicon control rectifier, |  |  | Select
Current limit type with isolate transfomer
|  | [ ] | Other _____________________
c. | Model/Cat. No. | LFB3-048-200 |  |  |  | Text
d. | Applied standard | NEMA-PE5, DIN41773 |  |  |  | Text
e. | AC input
| - No. of phase | 3 Phase, 3 Wire |  |  | Phase | Digit
| - Voltage range (line to line) | 380+ / -10% |  |  | V | Digit
| - Maximum current per phase | 28 |  |  | A | Digit
| - Line frequency range | 47.5-52.5 |  |  | Hz | Digit
| - Protection | [X] | Transient voltage protection, The maximum |  |  | Select
current @ 8/20 µs not less than 15 kA.(MOV)
|  | [X] | Circuit breaker with thermal magnetic trip
|  | [X] | Other | Ground bus for grouding system
f. | DC output
| - Rate current | 200 |  |  | A | Digit
| - Protection | [X] | Transient voltage protection, The maximum |  |  | Select
current @ 8/20 µs not less than 15 kA.(MOV)
|  | [X] | Circuit breaker with thermal magnetic trip
|  | [X] | Current limited at 110% of rated output current
|  | [ ] | Other _____________________
| - DC output voltage |  | 48 |  | V | Digit
| - Ripple voltage output |  | Not exceed 1 |  | % | Digit
| - Voltage regulation |  | ±1 |  | % | Digit
g. | Efficiency at full load |  | ≥85 |  | % | Digit
h. | Powerf factor at fulload |  | ≥80 |  | % | Digit
i. | Allowable mimimum battery voltage before charge |  | 30 |  | V | Digit
j. | Float voltage adjustment range | 40 | to | 65 | V | Digit
k. | Equalizing voltage adjustment range | 40 | to | 65 | V | Digit
l. | Ambient temperature |  | 0-40 |  | Co | Digit
m. | Relative humidity |  | 95 |  | % | Digit
n. | Parallel operation permission | [X] | Yes | [ ] No |  | Yes No
o. | Cooling method | [ ] | Fan | [X] Natural |  | Select
p. | DC output metering | [X] | Digital | [ ] Analog |  | Select
| - Class |  | 0.5 |  |  | Digit
q. | Alarm function | [X] | Loss of AC input alarm |  |  | Select
|  | [X] | Charge fail alarm |  |  | Select
|  | [X] | Low voltage alarm |  | (47 V; Range …40-48…V) | Select and Digit
|  | [X] | High voltage alarm |  | (57 V; Range …57-65…V) | Select and Digit
|  | [X] | Low Battery alarm |  | (43.2 V; Range …40-48…V) | Select and Digit
|  | [X] | Common alarm |  |  | Select
|  | [X] | Other _____________________ | Ethernet interface |  | Select
r. | Management | [X] | Float-Equalize charge. |  |  | Select
|  | [X] | Other _____________________ | >400 |  | Select
s. | Monitoring point | [X] | Alarm |  |  | Select
|  | [X] | Charge mode |  |  | Select
|  | [X] | Current and Voltage from charge's front panel. |  |  | Select
|  | [X] | Other | Ethernet interfacr |  | Select
t. | Storage |  | >400 |  | event | Digit
u. | Dimension
| - Length |  | 800 |  | mm | Digit
| - Width |  | 800 |  | mm | Digit
| - Height |  | 1800 |  | mm | Digit
v. | Weight |  | 500 |  | kg | Digit
w. | Floor loading |  | 957.3 |  | kg/sq m | Digit
x. | Ingress protection (IP) Class |  | IP21 |  |  | Digit

## SS-1AB4_SST (hidden)
SUBSTATION STEEL STRUCTURE
FORM PD 803
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  | 1AB4, 1AB7, 1AB14
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB4-2, 1AB7-10, 1AB7-11, 1AB14-1-1AB14-9
1AB1AB7-10
AB
a. | Manufacturer / Country
|  | - Fabrication |  | SIAM STEEL TOWER CO.,LTD./ THAILAND
|  | - Hot Dip Galvanizing |  | SIAM STEEL GALVANIZING CO.,LTD./ THAILAND
b. | Applied Standards
|  | - Mild Strength Structural Steel |  | JIS G3101 SS400 or ASTM A36 or Equivalent
|  | - High Strength Structural Steel |  | JIS G3101 SS540 or ASTM A572 Gr.50 or Equivalent
|  | - Base Plate |  | JIS G3101 SS400 or ASTM A36 or Equivalent
|  | - Anchor Bolt |  | JIS G3101 SS400 or ASTM A36 or Equivalent
|  | - Steel Pipe |  | JIS G3444 STK 400 or Equivalent
|  | - Step Bolt |  | ASTM A307 or Equivalent
|  | - Connection Bolt and Nut |  | ASTM A394 Type0 or Equivalent
|  | - Filler |  | JIS G3101 SS400 or Equivalent
|  | - Spring Washer |  | ASA B27.1 Regular Type or Equivalent
c. | Galvanizing Coating Weight
- Structural Steel and Steel Plate
Thickness 6 mm and over
|  | average |  | 715 | g/m2, or | 100 | mm
|  | minimum |  | 610 | g/m2, or | 86 | mm
Thickness under 6 mm
|  | average |  | 610 | g/m2, or | 86 | mm
|  | minimum |  | 550 | g/m2, or | 77 | mm
- Steel Pipe
|  | average |  | 550 | g/m2, or | 77 | mm
|  | minimum |  | 490 | g/m2, or | 69 | mm
- All Bolts and Nuts
|  | average |  | 385 | g/m2, or | 54 | mm
|  | minimum |  | 305 | g/m2, or | 43 | mm
- Washer and Filler
Thickness 5 mm and over
|  | average |  | 385 | g/m2, or | 54 | mm
|  | minimum |  | 305 | g/m2, or | 43 | mm
Thickness under 5 mm
|  | average |  | 305 | g/m2, or | 43 | mm
|  | minimum |  | 259 | g/m2, or | 37 | mm
Note. In case the materials conforming to EGAT’s drawings are not available in Thailand, the contractor shall submit modification drawings and/or calculation sheet of substitute materials to EGAT for approval before fabrication.

## Lamp post-1AB19_L&E (hidden)
TAPERED GALVANIZED STEEL LAMP POST
FORM PD 611.1
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB19
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB19-3
a. | Manufacturer / Country
| - Fabrication |  |  | NESCO LIGHTING & POLE CO.,LTD/ THAILAND
| - Hot Dip Galvanizing |  |  | WORLD COATING PROCESS CO.,LTD/ THAILAND
b. | Applied Standards
| - Structural Steel |  |  | JIS G3101 SS400
| - Anchor Bolt and Nut |  |  | JIS G3101 SS400
| - Washer |  |  | JIS G3101 SS400
| - Hot Dip Galvanizing |  |  | American Standards (ASTM)
A123: A153/A153M

## StreetLED-1AB19_L&E (hidden)
LED STREET LIGHTING FIXTURE
FORM PD 612.2(L)
Aug.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB19
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB19-2
a. | Applied Standards |  |  | TIS. 1955-2551, IEC 60598
b. | Lighting Fixture
| - Manufacturer / Country |  |  | L&E Manufacturing co.,Ltd/ Thailand
| - Type / Model / Cat. No. |  |  | L&E # SLL 650-50LED
- Material
|  | - Housing |  | Die-Cast Aluminium
|  | - Front Cover |  | Clear toughened glass (Heat shock resistance glass)
| - Degree of protection |  |  | IP 66
| - Dimension (approx.) |  |  | 228x578x135 |  | mm
| - Weight (approx.) |  |  | 6 |  | kg
c. | LED
| - Power |  |  | 50 |  | W
| - Color Rendering Index (CRI) |  |  | 70
| - Correlated Color Temperature (CCT) |  |  | 5700 |  | K
d. | Driver
| - Rated Voltage / Frequency / Watt |  |  | 100-240V/50/60Hz/75W |  | V/Hz/W
| - Power Factor |  |  | >95 |  | %
e. | Luminaire Efficacy |  |  | 160 |  | lm/W
f. | Service Life |  |  | 50000 |  | h

## FloodLED-1AB19_L&E (hidden)
LED FLOOD LIGHTING FIXTURE
FORM PD 611.1(L)
Aug. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB19
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB19-1
a. | Applied Standards |  |  | TIS. 1955-2551, IEC 60598
b. | Lighting Fixture
| - Manufacturer / Country |  |  | L&E Manufacturing co.,Ltd/ Thailand
| - Type / Model / Cat. No. |  |  | L&E # FLL 435-110LED
- Material
|  | - Housing |  | Die-Cast Aluminium
|  | - Front Cover |  | Clear heat resistance glass
|  | - Mounting Bracket |  | Painted steel
| - Degree of protection |  |  | IP 66
| - Dimension (approx.) |  |  | 250x81x444 |  | mm
| - Weight (approx.) |  |  | 5.6 |  | kg
c. | LED
| - Power |  |  | 110 |  | W
| - Color Rendering Index (CRI) |  |  | 70
| - Correlated Color Temperature (CCT) |  |  | 5700 |  | K
d. | Driver
| - Rated Voltage / Frequency / Watt |  |  | 100-305VAC/50Hz/110W |  | V/Hz/W
| - Power Factor |  |  | 98 |  | %
e. | Luminaire Efficacy |  |  | 135 |  | lm/W
f. | Service Life |  |  | 50000 |  | h

## AB23_GPT (hidden)
SUBSTATION MISCELLANEOUS
FORM PD AB23
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB23
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB23-1,AB23-2,1AB23-3,1AB23-5
a. | Manufacturer / Country
| - Rigid Steel Conduit |  |  | PAT / THAILAND
| - Fittings for Rigid Steel Conduit |  |  | STEEL CITY/T T T STEEL INDUSTRY/Thailand
| - HDPE Conduit |  |  | TGG / Thailand
| - Fittings For HDPE Conduit |  |  | TGG / Thailand
| - Heat Shrinkable Insulation Material |  |  | TE/ GERMANY
(For Medium Voltage)
Note. Catalog of the following equipment shall be submitted for preliminary consideration. Actual type (such as size, length etc.) shall be submitted for approval after design stage.
| - | Rigid Steel Conduit and fittings
| - | HDPE Conduit and fittings
| - | Heat Shrinkable Insulation Material

## outdr ter 33blow_GPT
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | 3M
|  | - Country of origin |  | USA
b. | Type / Model / Cat. NO. |  |  | Cold Shrink/QTII 5652/No1
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Silicone Rubber
e. | Rated Voltage |  |  | Insulation Class 25 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 21.5 |  |  |  | kV
i. | Operating Environments |  |  | Heavy Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 35 | mm2 |  | Max | 120 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 21.3 | mm |  | Max | 35 | mm
Note: Although the conductor size range in this proposal does not conform to the XLPE proposal data, the cable termination is still suitable for use with the proposed XLPE cables.
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X

## outdr ter 33blow_GK
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | TE Connectivity, Ltd.
|  | - Country of origin |  | USA
b. | Type / Model / Cat. NO. |  |  | TFT252E/SG
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Elastomeric Polymer (Silicone rubber)
e. | Rated Voltage |  |  | Insulation Class 25 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 21.5 |  |  |  | kV
i. | Operating Environments |  |  | Heavy Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 35 | mm2 |  | Max | 95 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 16 | mm |  | Max | 28 | mm
Note: Although the conductor size range in this proposal does not conform to the XLPE proposal data, the cable termination is still suitable for use with the proposed XLPE cables.
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X

## cleat 33 kV Trefoil_CMP
CABLE CLEATS
PD 326.CC
[10 empty] | Dec.2024 | [5 empty] | รายการตรวจ Cable cleat
PROPOSAL DATA | [11 empty] | comment |  |  | 1 | Material
PROCUREMENT REFERENCE |  |  | HSIS-S-01 |  | SCHEDULE NO. |  |  | 1AB16 |  |  |  | waiting for discussion with P'Ja |  |  |  | 1.1 | Metallic: | ALUMINUM 5000 SERIES
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  |  | ITEM NO. |  | 1AB16-2 | [10 empty] | SS316L Stainless steel
[16 empty] | 1.2 | Composite:
[18 empty] | Metalic part | ALUMINUM 5000 SERIES
SS316L Stainless steel
a. | Manufacturer and Country of Origin | [16 empty] | non-metallic part | ANY
|  | - Manufacturer |  |  | CMP PRODUCTS
|  | - Country of origin |  |  | UNITED KINGDOM | [9 empty] | 2 | Force/1Cleat must be more than RF EGAT
[12 empty] | ปรับให้พิจารณาแค่ type โดยขนาดของ cleat |  |  |  | 2.1 | FLAT
b. | Type/Model[1] |  |  |  | PATRIOT-HT (SDSS) SDSS030035HT | [6 empty] | จะพิจารณาในขั้นบริหารสัญญา | [5 empty] | Calculated result | #REF!
c. | For XLPE Cable Suitability[1] | [10 empty] | ตัดออกเนื่องจากพิจารณาขนาด
| - Overall Diameter Range |  |  |  | Min | 30 | mm. |  | Max | 35 | mm. | ในขั้นบริหารสัญญา
d. | Applied Standard |  |  |  | conforming with EGAT requirement (IEC 61914)
*in case of other, please specify in the box below:
e. | Classification according to material[2] |  |  |  |  | Metallic | [5 empty] | แก้รูปแบบ
Material :
[5 empty] | X | Composite
[6 empty] | Material : | 316L Stainless Steel | [9 empty] | EGAT
[6 empty] | and | with Standard Polymer Liner Standard Polymer Liners are classified as Low Smoke and Fume Zero Halogen (LSF0H), Phosphorus-free | [9 empty] | V | I short circuit | Lineal Spacing | FLAT Force | TREFOIL Force
f. | Resistant to electromechanical forces, withstanding more than one short circuit[3] | [15 empty] | 230 | 170 |  | #REF! | #REF!
| - Cable centre spacing (S) |  |  |  | 36 |  | mm |  |  |  |  | 0.16 | 0.17 | #REF! |  |  |  | Force
| - The peak short circuit current of the 2nd shortcircuit |  |  |  | 108 |  | kA |  |  |  |  | Trefoil wtihstrand force | [5 empty] | #REF!
| - Lineal spacing (D) |  |  |  | 600 |  | mm |  |  |  |  | Flat force withstrand force
g. | Formation |  |  |  | Trefoil | [6 empty] | ขอย้ายไปด้านบนได้ไหม
| Note [1]: | The exact size of Cable Cleat shall be confirmed after the exact overall diameter of XLPE power cable is confirmed during project stage. | [9 empty] | เพิ่มเพื่อความชัดเจน
| Note [2]: | Definitions comply with IEC 61914. metallic consisting of metal only. composite consisting of metallic and non-metallic materials.
a) Fibre reinforced resin materials are not considered to be composite.
b) Materials include any materials supplied by the manufacturer as part of a cable cleat or intermediate restraint or with a cable cleat or intermediate restraint in the same packaging. This may include fixings such as nuts, bolts, screws, washers, springs and pins.
| Note [3]: | The data specified in this item shall conform to the Type Test Report of the type proposed.
| Note [4]: | The values shall be based on the same cables and conditions of the test for resistance to electromechanical forces specified in IEC 61914.
| conforming with EGAT requirement (IEC 61914) |  |  | Trefoil
| Other |  |  | Flat
Metallic
| Composite |  |  | X

## XLPE_BCC
115 kV and below XLPE POWER CABLE
FORM PD 322
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB17
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  |  | ITEM NO. |  | 1AB17-1
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  |  | Bangkok Cable Co., Ltd.
|  | - Country of origin |  |  | Thailand
b. | Type / Model / Cat. NO. |  |  |  | CV(TS)
c. | Applied Standard |  |  |  | conforming with EGAT requirement ( ICEA Pub. No S-93-639)
*in case of other, please specify in the box below :
d. | Voltage Class |  |  |  | 25 |  |  |  |  | kV
e. | Calculated Cross-Sectional Area of Stranded Conductor |  |  |  | 35.7 |  |  |  |  | mm2
|  | - Material of Conductor |  |  | Copper
|  | - No. of Wires in the Stranded Conductor |  |  | 7
|  | - Diameter of Each Wire |  |  | 2.65 |  |  |  |  | mm
f. | Outside Diameter of Stranded Conductor |  |  |  | Min | 6.88 | mm |  | Max | 7.02 | mm
g. | Conductor Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.6 | mm
h. | Insulation |  | (Material / Thickness) |  | XLPE |  |  |  | / | 8.76 | mm
i. | Insulation Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.7 | mm
j. | Outside Diameter of Insulation with |  |  |  | Min | 25.5 | mm |  | Max | 27.5 | mm
Extruded Semi-Conducting Insulation Screen (min-max)
k. | Metal Screen/Sheath |  | (Material / Thickness) |  | Copper tape |  |  |  | / | 0.1 | mm
l. | Cushion |  | (Material / Thickness) |  | Polyester Non-Woven Tape |  |  |  | / | 0.1 | mm
m. | Oversheath (Jacket) |  | (Material / Thickness) |  | PVC |  |  |  | / | 2.03 | mm
n. | Overall Diameter (min-max) |  |  |  | Min | 31 | mm |  | Max | 35 | mm
o. | Impulse Withstand Voltage (BIL) |  |  |  | 150 | [5 empty] | kV
p. | (1) Ampacity of conductor in Free Air, Flat Formation with Spacing 1 Time Diameter [1] | [7 empty] | 200 |  | A
| (2) Ampacity of conductor for Direct Burial, Flat Formation with Spacing 1 Time Diameter, | [7 empty] | 160 |  | A
Depth of Laying in Ground 0.4 m, Soil Thermal Resistivity 1.2°C-m/watt [1]
q. | Min Bending Radius as a Multiple of Cable Diameter
|  | - During installation |  |  | 10 |  |  |  |  | Times
|  | - After Installation |  |  | 10 |  |  |  |  | Times
r. | Max Resistance at 20 °C of Conductor |  |  |  | 0.524 |  |  |  |  | Ω/km
s. | Length of Cable per Reel |  |  |  | 500 |  |  |  |  | m
Note [1]: |  | Conductor Temperature not in Excess of 90°C at 100% Load Factor and at an Ambient Temperature of 45°C
Note [2]: |  | Drawing and dimension of Cable Reels/Drums together with packing details shall be submitted during project stage for EGAT approval.
conforming with EGAT requirement ( ICEA Pub. No S-93-639)
conforming with EGAT requirement (TIS 2202)
conforming with EGAT requirement (IEC 62067)
Other*

## LV_Turnkey-1AB18_BCC
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD-LV Cable & Con
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB18
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB18-1, 1AB18-2, 1AB18-3, 1AB18-4, 1AB18-5, 1AB18-6, 1AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2559) |  | conforming with EGAT requirement (TIS838-2531) |  | conforming with EGAT requirement (TIS838-2531)
*in case of other, please specify in the box below :
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
|  | - Manufacturer |  | Bangkok Cable Co., Ltd. |  |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand |  |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2553) |  |  | conforming with EGAT requirement (TIS11-2559)
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B3, ASTM B8)
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | Sinthani Industry Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM A363)
*in case of other, please specify in the box below :
e. | Aluminum Conductor
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B231, ASTM B232)
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other

## LV_Turnkey-1AB18_USHA
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD-LV Cable & Con
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB18
BIDDER |  | PWH (THAILAND) COMPANY LIMITED |  | ITEM NO. | 1AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
- Manufacturer
- Country
- Applied Standards
*in case of other, please specify in the box below :
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
- Manufacturer
- Country
- Applied Standards
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
- Manufacturer
- Country
- Applied Standards
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | Usha Siam Steel Industries Public Company Limeted
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM A363)
*in case of other, please specify in the box below :
e. | Aluminum Conductor
- Manufacturer
- Country
- Applied Standards
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other