## XLPE
115 kV and below XLPE POWER CABLE
FORM PD 322
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | RTS3-S-02 | SCHEDULE NO. |  |  |  | 1AB17
BIDDER |  | DEMCO Public Company Limited |  |  | ITEM NO. |  | 1AB17-1
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  |  | Pheplps Dodge International (Thailand) Ltd.
|  | - Country of origin |  |  | Thailand
b. | Type / Model / Cat. NO. |  |  |  | 25kV CU/XLPE/CTS/PVC
c. | Applied Standard |  |  |  | conforming with EGAT requirement ( ICEA Pub. No S-93-639)
*in case of other, please specify in the box below :
d. | Voltage Class |  |  |  | 25 |  |  |  | kV
e. | Calculated Cross-Sectional Area of Stranded Conductor |  |  |  | 33.6 |  |  |  | mm2
|  | - Material of Conductor |  |  | Annealed Copper
|  | - No. of Wires in the Stranded Conductor |  |  | 7
|  | - Diameter of Each Wire |  |  | 2.65-2.71 |  |  |  | mm
f. | Outside Diameter of Stranded Conductor |  |  |  | Min | 6.85 | mm | Max | 7.02 | mm
g. | Conductor Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  | / | 0.6 | mm
h. | Insulation |  | (Material / Thickness) |  | XLPE |  |  | / | 8.76 | mm
i. | Insulation Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  | / | 0.6 | mm
j. | Outside Diameter of Insulation with |  |  |  | Min | 26.7 | mm | Max | 29.8 | mm
Extruded Semi-Conducting Insulation Screen (min-max)
k. | Metal Screen/Sheath |  | (Material / Thickness) |  | Copper tape |  |  | / | 0.1 | mm
l. | Cushion |  | (Material / Thickness) |  | Polyester non-woven tape (Spunbond tape) |  |  | / | 0.2 | mm
m. | Oversheath (Jacket) |  | (Material / Thickness) |  | Black PVC |  |  | / | 2.03 | mm
n. | Overall Diameter (min-max) |  |  |  | Min | 31 | mm | Max | 35 | mm
o. | Impulse Withstand Voltage (BIL) |  |  |  | 150 |  |  |  |  | kV
p. | (1) Ampacity of conductor in Free Air, Flat Formation with Spacing 1 Time Diameter [1] | [6 empty] | 198 |  | A
| (2) Ampacity of conductor for Direct Burial, Flat Formation with Spacing 1 Time Diameter, | [6 empty] | 162 |  | A
Depth of Laying in Ground 0.4 m, Soil Thermal Resistivity 1.2°C-m/watt [1]
q. | Min Bending Radius as a Multiple of Cable Diameter
|  | - During installation |  |  | 20 |  |  |  | Times
|  | - After Installation |  |  | 15 |  |  |  | Times
r. | Max Resistance at 20 °C of Conductor |  |  |  | 0.524 |  |  |  | Ω/km
s. | Length of Cable per Reel |  |  |  | 1000 |  |  |  | m
Note [1]: |  | Conductor Temperature not in Excess of 90°C at 100% Load Factor and at an Ambient Temperature of 45°C
Note [2]: |  | Drawing and dimension of Cable Reels/Drums together with packing details shall be submitted during project stage for EGAT approval.
conforming with EGAT requirement ( ICEA Pub. No S-93-639)
conforming with EGAT requirement (TIS 2202)
conforming with EGAT requirement (IEC 62067)
Other*