## outdr ter 33blow - TE
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | ITALTHAI ENGINEERING CO., LTD. / Thailand |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | TE Connectivity, Ltd.
|  | - Country of origin |  | USA
b. | Type / Model / Cat. NO. |  |  | TFT-252E/SG
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Elastomeric Polymer (Silicone rubber)
e. | Rated Voltage |  |  | Insulation Class 25 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 21.5 |  |  |  | kV
i. | Operating Environments |  |  | Heavy Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 35 | mm2 |  | Max | 95 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 16 | mm |  | Max | 28 | mm
Please recheck Insulation Diameter and confirm ; 28 mm is not conform to the proposed AB17 XLPE cable (29)
Note: Although the conductor size range in this proposal does not conform to the XLPE proposal data, the cable termination is still suitable for use with the proposed XLPE cables.
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X

## LV_Tunrkey-Bangkok Cable
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD-LV Cable & Con
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB18
BIDDER |  | ITALTHAI ENGINEERING CO., LTD. / Thailand |  | ITEM NO. | 1AB18-1, 1AB18-2, 1AB18-3, 1AB18-4, 1AB18-5, 1AB18-6 & 1AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2559) |  | conforming with EGAT requirement (TIS838-2531)
*in case of other, please specify in the box below :
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
|  | - Manufacturer |  | Bangkok Cable Co., Ltd. |  |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand |  |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2553) |  |  | conforming with EGAT requirement (TIS11-2559)
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B3, ASTM B8)
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | Sinthani Industry Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM A363)
*in case of other, please specify in the box below :
e. | Aluminum Conductor
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B231, ASTM B232)
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other