## NoeyCleat
CABLE CLEATS
PD 326.CC
[10 empty] | Dec.2024 | [5 empty] | รายการตรวจ Cable cleat
PROPOSAL DATA | [11 empty] | comment |  |  | 1 | Material
PROCUREMENT REFERENCE |  |  | HSIS-S-01 |  | SCHEDULE NO. |  |  | 1AB16 |  |  |  | waiting for discussion with P'Ja |  |  |  | 1.1 | Metallic: | ALUMINUM 5000 SERIES
BIDDER |  | NongNoey |  |  | ITEM NO. |  | 1AB16-2 | [10 empty] | SS316L Stainless steel
[16 empty] | 1.2 | Composite:
[18 empty] | Metalic part | ALUMINUM 5000 SERIES
SS316L Stainless steel
a. | Manufacturer and Country of Origin | [16 empty] | non-metallic part | ANY
|  | - Manufacturer |  |  | Rynchong Corp
|  | - Country of origin |  |  | Australia | [9 empty] | 2 | Force/1Cleat must be more than RF EGAT
[12 empty] | ปรับให้พิจารณาแค่ type โดยขนาดของ cleat |  |  |  | 2.1 | FLAT
b. | Type/Model[1] |  |  |  | PATRIOT-HT (SDSS) SDSS030035HT | [6 empty] | จะพิจารณาในขั้นบริหารสัญญา | [5 empty] | Calculated result | #REF!
c. | For XLPE Cable Suitability[1] | [10 empty] | ตัดออกเนื่องจากพิจารณาขนาด
| - Overall Diameter Range |  |  |  | Min | 30 | mm. |  | Max | 35 | mm. | ในขั้นบริหารสัญญา
d. | Applied Standard |  |  |  | conforming with EGAT requirement (IEC 61914)
*in case of other, please specify in the box below:
e. | Classification according to material[2] |  |  |  |  | Metallic | [5 empty] | แก้รูปแบบ
Material :
[5 empty] | X | Composite
[6 empty] | Material : | 316L Stainless Steel | [9 empty] | EGAT
[6 empty] | and | with Standard Polymer Liner Standard Polymer Liners are classified as Low Smoke and Fume Zero Halogen (LSF0H), Phosphorus-free | [9 empty] | V | I short circuit | Lineal Spacing | FLAT Force | TREFOIL Force
f. | Resistant to electromechanical forces, withstanding more than one short circuit[3] | [15 empty] | 230 | 170 |  | #REF! | #REF!
| - Cable centre spacing (S) |  |  |  | 36 |  | mm |  |  |  |  | 0.16 | 0.17 | #REF! |  |  |  | Force
| - The peak short circuit current of the 2nd shortcircuit |  |  |  | 108 |  | kA |  |  |  |  | Trefoil wtihstrand force | [5 empty] | #REF!
| - Lineal spacing (D) |  |  |  | 600 |  | mm |  |  |  |  | Flat force withstrand force
g. | Formation |  |  |  | Trefoil | [6 empty] | ขอย้ายไปด้านบนได้ไหม
| Note [1]: | The exact size of Cable Cleat shall be confirmed after the exact overall diameter of XLPE power cable is confirmed during project stage. | [9 empty] | เพิ่มเพื่อความชัดเจน
| Note [2]: | Definitions comply with IEC 61914. metallic consisting of metal only. composite consisting of metallic and non-metallic materials.
a) Fibre reinforced resin materials are not considered to be composite.
b) Materials include any materials supplied by the manufacturer as part of a cable cleat or intermediate restraint or with a cable cleat or intermediate restraint in the same packaging. This may include fixings such as nuts, bolts, screws, washers, springs and pins.
| Note [3]: | The data specified in this item shall conform to the Type Test Report of the type proposed.
| Note [4]: | The values shall be based on the same cables and conditions of the test for resistance to electromechanical forces specified in IEC 61914.
| conforming with EGAT requirement (IEC 61914) |  |  | Trefoil
| Other |  |  | Flat
Metallic
| Composite |  |  | X

## NoeyTerm
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | NongNoey |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | DadarMfg
|  | - Country of origin |  | Mexico
b. | Type / Model / Cat. NO. |  |  | Cold Shrink/QTII 5652/No1
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Silicone Rubber
e. | Rated Voltage |  |  | Insulation Class 25 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 22 |  |  |  | kV
i. | Operating Environments |  |  | Heavy Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 35 | mm2 |  | Max | 120 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 21.3 | mm |  | Max | 35 | mm
Note: Although the conductor size range in this proposal does not conform to the XLPE proposal data, the cable termination is still suitable for use with the proposed XLPE cables.
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X

## Noey17
115 kV and below XLPE POWER CABLE
FORM PD 322
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB17
BIDDER |  | NongNoey |  |  | ITEM NO. |  | 1AB17-1
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  |  | Rynchong
|  | - Country of origin |  |  | Thailand
b. | Type / Model / Cat. NO. |  |  |  | CV(TS)
c. | Applied Standard |  |  |  | conforming with EGAT requirement ( ICEA Pub. No S-93-639)
*in case of other, please specify in the box below :
d. | Voltage Class |  |  |  | 25 |  |  |  |  | kV
e. | Calculated Cross-Sectional Area of Stranded Conductor |  |  |  | 35.7 |  |  |  |  | mm2
|  | - Material of Conductor |  |  | Silver
|  | - No. of Wires in the Stranded Conductor |  |  | 7
|  | - Diameter of Each Wire |  |  | 2.65 |  |  |  |  | mm
f. | Outside Diameter of Stranded Conductor |  |  |  | Min | 6.88 | mm |  | Max | 7.02 | mm
g. | Conductor Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.6 | mm
h. | Insulation |  | (Material / Thickness) |  | XLPE |  |  |  | / | 8.76 | mm
i. | Insulation Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.7 | mm
j. | Outside Diameter of Insulation with |  |  |  | Min | 25.5 | mm |  | Max | 27.5 | mm
Extruded Semi-Conducting Insulation Screen (min-max)
k. | Metal Screen/Sheath |  | (Material / Thickness) |  | Copper tape |  |  |  | / | 0.1 | mm
l. | Cushion |  | (Material / Thickness) |  | Polyester Non-Woven Tape |  |  |  | / | 0.1 | mm
m. | Oversheath (Jacket) |  | (Material / Thickness) |  | PVC |  |  |  | / | 2.03 | mm
n. | Overall Diameter (min-max) |  |  |  | Min | 31 | mm |  | Max | 35 | mm
o. | Impulse Withstand Voltage (BIL) |  |  |  | 150 | [5 empty] | kV
p. | (1) Ampacity of conductor in Free Air, Flat Formation with Spacing 1 Time Diameter [1] | [7 empty] | 200 |  | A
| (2) Ampacity of conductor for Direct Burial, Flat Formation with Spacing 1 Time Diameter, | [7 empty] | 160 |  | A
Depth of Laying in Ground 0.4 m, Soil Thermal Resistivity 1.2°C-m/watt [1]
q. | Min Bending Radius as a Multiple of Cable Diameter
|  | - During installation |  |  | 10 |  |  |  |  | Times
|  | - After Installation |  |  | 10 |  |  |  |  | Times
r. | Max Resistance at 20 °C of Conductor |  |  |  | 0.524 |  |  |  |  | Ω/km
s. | Length of Cable per Reel |  |  |  | 500 |  |  |  |  | m
Note [1]: |  | Conductor Temperature not in Excess of 90°C at 100% Load Factor and at an Ambient Temperature of 45°C
Note [2]: |  | Drawing and dimension of Cable Reels/Drums together with packing details shall be submitted during project stage for EGAT approval.

## Noey18
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD-LV Cable & Con
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB18
BIDDER |  | NongNoey |  | ITEM NO. | 1AB18-1, 1AB18-2, 1AB18-3, 1AB18-4, 1AB18-5, 1AB18-6, 1AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
|  | - Manufacturer |  | Phelph Dodge
|  | - Country |  | Japan
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2559) |  | conforming with EGAT requirement (TIS838-2531)
*in case of other, please specify in the box below :
ABC
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
|  | - Manufacturer |  | DaphneCho |  |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand |  |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2553) |  |  | conforming with EGAT requirement (TIS11-2559)
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B3, ASTM B8)
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | DaphneCho
|  | - Country |  | Thailand
|  | - Applied Standards |  | Other
*in case of other, please specify in the box below :
ASDF
e. | Aluminum Conductor
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailnad
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B231, ASTM B232)
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other

## Thailnad
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD-LV Cable & Con
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB18
BIDDER |  | ViRYN |  | ITEM NO. | 1AB18-1, 1AB18-2, 1AB18-3, 1AB18-4, 1AB18-5, 1AB18-6, 1AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
|  | - Manufacturer |  | DaphneCho
|  | - Country |  | Japan
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2559) |  | conforming with EGAT requirement (TIS838-2531)
*in case of other, please specify in the box below :
ABC
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
|  | - Manufacturer |  | DaphneCho |  |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand |  |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2553) |  |  | conforming with EGAT requirement (TIS11-2559)
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B3, ASTM B8)
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | DaphneCho
|  | - Country |  | Thailand
|  | - Applied Standards |  | Other
*in case of other, please specify in the box below :
ASDF
e. | Aluminum Conductor
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailnad
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B231, ASTM B232)
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other

## LV_Turnkey
`
LOW VOLTAGE CABLE AND CONDUCTOR
FORM PD-LV Cable & Con
Oct.2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. | 1AB18
BIDDER |  | ViRYN |  | ITEM NO. | 1AB18-1, 1AB18-2, 1AB18-3, 1AB18-4, 1AB18-5, 1AB18-6, 1AB18-7
a. | Power Cable and Control Cable |  |  | Power Cable |  | Control Cable |  | Twisted Pair Control Cable
|  | - Manufacturer |  | DaphneCho
|  | - Country |  | Japan
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2559) |  | conforming with EGAT requirement (TIS838-2531)
*in case of other, please specify in the box below :
b. | Lighting cable (THW and/or NYY) |  |  | THW (IEC01) |  |  | NYY
|  | - Manufacturer |  | DaphneCho |  |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand |  |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (TIS11-2553) |  |  | conforming with EGAT requirement (TIS11-2559)
*in case of other, please specify in the box below :
c. | Annealed Copper Ground Wire
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B3, ASTM B8)
*in case of other, please specify in the box below :
d. | Overhead Ground Wire
|  | - Manufacturer |  | DaphneCho
|  | - Country |  | Thailand
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM A363)
*in case of other, please specify in the box below :
e. | Aluminum Conductor
|  | - Manufacturer |  | Bangkok Cable Co., Ltd.
|  | - Country |  | Japan
|  | - Applied Standards |  | conforming with EGAT requirement (ASTM B231, ASTM B232)
*in case of other, please specify in the box below :
| Note: Routine tests and/or Quality Conformance Tests are required for equipment in a, b, and c. | [8 empty] | << optional in case of tests are required
conforming with EGAT requirement (TIS11-2559)
Other
conforming with EGAT requirement (TIS838-2531)
Other
conforming with EGAT requirement (TIS11-2553)
Other
conforming with EGAT requirement (ASTM B231, ASTM B232)
Other
conforming with EGAT requirement (ASTM B3, ASTM B8)
Other
conforming with EGAT requirement (ASTM A363)
Other

## XLPE
115 kV and below XLPE POWER CABLE
FORM PD 322
Aug. 2025
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB17
BIDDER |  | ViRYN |  |  | ITEM NO. |  | 1AB17-1
a. | Manufacturer and Country of Origin
|  | - Manufacturer |  |  | Rynchong
|  | - Country of origin |  |  | Thailand
b. | Type / Model / Cat. NO. |  |  |  | CV(TS)
c. | Applied Standard |  |  |  | conforming with EGAT requirement ( ICEA Pub. No S-93-639)
*in case of other, please specify in the box below :
d. | Voltage Class |  |  |  | 25 |  |  |  |  | kV
e. | Calculated Cross-Sectional Area of Stranded Conductor |  |  |  | 35.7 |  |  |  |  | mm2
|  | - Material of Conductor |  |  | Silver
|  | - No. of Wires in the Stranded Conductor |  |  | 7
|  | - Diameter of Each Wire |  |  | 2.65 |  |  |  |  | mm
f. | Outside Diameter of Stranded Conductor |  |  |  | Min | 6.88 | mm |  | Max | 7.02 | mm
g. | Conductor Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.6 | mm
h. | Insulation |  | (Material / Thickness) |  | XLPE |  |  |  | / | 8.76 | mm
i. | Insulation Screen |  | (Material / Thickness) |  | Semi-conductive XLPE |  |  |  | / | 0.7 | mm
j. | Outside Diameter of Insulation with |  |  |  | Min | 25.5 | mm |  | Max | 27.5 | mm
Extruded Semi-Conducting Insulation Screen (min-max)
k. | Metal Screen/Sheath |  | (Material / Thickness) |  | Copper tape |  |  |  | / | 0.1 | mm
l. | Cushion |  | (Material / Thickness) |  | Polyester Non-Woven Tape |  |  |  | / | 0.1 | mm
m. | Oversheath (Jacket) |  | (Material / Thickness) |  | PVC |  |  |  | / | 2.03 | mm
n. | Overall Diameter (min-max) |  |  |  | Min | 31 | mm |  | Max | 35 | mm
o. | Impulse Withstand Voltage (BIL) |  |  |  | 150 | [5 empty] | kV
p. | (1) Ampacity of conductor in Free Air, Flat Formation with Spacing 1 Time Diameter [1] | [7 empty] | 200 |  | A
| (2) Ampacity of conductor for Direct Burial, Flat Formation with Spacing 1 Time Diameter, | [7 empty] | 160 |  | A
Depth of Laying in Ground 0.4 m, Soil Thermal Resistivity 1.2°C-m/watt [1]
q. | Min Bending Radius as a Multiple of Cable Diameter
|  | - During installation |  |  | 10 |  |  |  |  | Times
|  | - After Installation |  |  | 10 |  |  |  |  | Times
r. | Max Resistance at 20 °C of Conductor |  |  |  | 0.524 |  |  |  |  | Ω/km
s. | Length of Cable per Reel |  |  |  | 500 |  |  |  |  | m
Note [1]: |  | Conductor Temperature not in Excess of 90°C at 100% Load Factor and at an Ambient Temperature of 45°C
Note [2]: |  | Drawing and dimension of Cable Reels/Drums together with packing details shall be submitted during project stage for EGAT approval.

## cleat 33 kV Trefoil_CMP
CABLE CLEATS
PD 326.CC
[10 empty] | Dec.2024 | [5 empty] | รายการตรวจ Cable cleat
PROPOSAL DATA | [11 empty] | comment |  |  | 1 | Material
PROCUREMENT REFERENCE |  |  | HSIS-S-01 |  | SCHEDULE NO. |  |  | 1AB16 |  |  |  | waiting for discussion with P'Ja |  |  |  | 1.1 | Metallic: | ALUMINUM 5000 SERIES
BIDDER |  | ViRYN |  |  | ITEM NO. |  | 1AB16-2 | [10 empty] | SS316L Stainless steel
[16 empty] | 1.2 | Composite:
[18 empty] | Metalic part | ALUMINUM 5000 SERIES
SS316L Stainless steel
a. | Manufacturer and Country of Origin | [16 empty] | non-metallic part | ANY
|  | - Manufacturer |  |  | Rynchong Corp
|  | - Country of origin |  |  | Australia | [9 empty] | 2 | Force/1Cleat must be more than RF EGAT
[12 empty] | ปรับให้พิจารณาแค่ type โดยขนาดของ cleat |  |  |  | 2.1 | FLAT
b. | Type/Model[1] |  |  |  | PATRIOT-HT (SDSS) SDSS030035HT | [6 empty] | จะพิจารณาในขั้นบริหารสัญญา | [5 empty] | Calculated result | #REF!
c. | For XLPE Cable Suitability[1] | [10 empty] | ตัดออกเนื่องจากพิจารณาขนาด
| - Overall Diameter Range |  |  |  | Min | 30 | mm. |  | Max | 35 | mm. | ในขั้นบริหารสัญญา
d. | Applied Standard |  |  |  | conforming with EGAT requirement (IEC 61914)
*in case of other, please specify in the box below:
e. | Classification according to material[2] |  |  |  |  | Metallic | [5 empty] | แก้รูปแบบ
Material :
[5 empty] | X | Composite
[6 empty] | Material : | 316L Stainless Steel | [9 empty] | EGAT
[6 empty] | and | with Standard Polymer Liner Standard Polymer Liners are classified as Low Smoke and Fume Zero Halogen (LSF0H), Phosphorus-free | [9 empty] | V | I short circuit | Lineal Spacing | FLAT Force | TREFOIL Force
f. | Resistant to electromechanical forces, withstanding more than one short circuit[3] | [15 empty] | 230 | 170 |  | #REF! | #REF!
| - Cable centre spacing (S) |  |  |  | 36 |  | mm |  |  |  |  | 0.16 | 0.17 | #REF! |  |  |  | Force
| - The peak short circuit current of the 2nd shortcircuit |  |  |  | 108 |  | kA |  |  |  |  | Trefoil wtihstrand force | [5 empty] | #REF!
| - Lineal spacing (D) |  |  |  | 600 |  | mm |  |  |  |  | Flat force withstrand force
g. | Formation |  |  |  | Trefoil | [6 empty] | ขอย้ายไปด้านบนได้ไหม
| Note [1]: | The exact size of Cable Cleat shall be confirmed after the exact overall diameter of XLPE power cable is confirmed during project stage. | [9 empty] | เพิ่มเพื่อความชัดเจน
| Note [2]: | Definitions comply with IEC 61914. metallic consisting of metal only. composite consisting of metallic and non-metallic materials.
a) Fibre reinforced resin materials are not considered to be composite.
b) Materials include any materials supplied by the manufacturer as part of a cable cleat or intermediate restraint or with a cable cleat or intermediate restraint in the same packaging. This may include fixings such as nuts, bolts, screws, washers, springs and pins.
| Note [3]: | The data specified in this item shall conform to the Type Test Report of the type proposed.
| Note [4]: | The values shall be based on the same cables and conditions of the test for resistance to electromechanical forces specified in IEC 61914.
| conforming with EGAT requirement (IEC 61914) |  |  | Trefoil
| Other |  |  | Flat
Metallic
| Composite |  |  | X

## MExico
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | ViRYN |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | DadarMfg
|  | - Country of origin |  | Mexico
b. | Type / Model / Cat. NO. |  |  | Cold Shrink/QTII 5652/No1
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Silicone Rubber
e. | Rated Voltage |  |  | Insulation Class 25 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 22 |  |  |  | kV
i. | Operating Environments |  |  | Heavy Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 35 | mm2 |  | Max | 120 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 21.3 | mm |  | Max | 35 | mm
Note: Although the conductor size range in this proposal does not conform to the XLPE proposal data, the cable termination is still suitable for use with the proposed XLPE cables.
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X

## China, Ruber, Med pol
33 kV and below CABLE TERMINATIONS (for outdoor termination)
FORM PD 326.MV
Nov. 2024
PROPOSAL DATA
PROCUREMENT REFERENCE |  |  | RTS3-S-02 | SCHEDULE NO. |  |  | 1AB16
BIDDER |  | ViRYN |  | ITEM NO. |  | 1AB16-1
a. | Manufacturer and Country of Origin
- Cable Terminations
|  | - Manufacturer |  | DadarMfg
|  | - Country of origin |  | China
b. | Type / Model / Cat. NO. |  |  | Cold Shrink/QTII 5652/No1
c. | Applied Standard |  |  | conforming with EGAT requirement (IEEE 48)
*in case of other, please specify in the box below :
d. | Material of Insulator |  |  | Silicone Ruber
e. | Rated Voltage |  |  | Insulation Class 15 kV | [5 empty] | kV
*in case of other, please specify in the box below :
f. | Impulse Withstand Voltage (BIL) |  |  | 150 |  |  |  | kV
g. | Power frequency (Dry) |  |  | 65 |  | kV | 1 | min
h. | Partial discharge |  |  | 22 |  |  |  | kV
i. | Operating Environments |  |  | Medium Pollution
*in case of other, please specify in the box below :
j. | Aerial Connector |  |  | 2 x 1 bolt holes NEMA Pad
*in case of other, please specify in the box below :
k. | For XLPE Cable Suitability
|  | - Conductor Range |  | Min | 35 | mm2 |  | Max | 120 | mm2
|  | - Insulation Diameter (min-max) |  | Min | 21.3 | mm |  | Max | 35 | mm
Note: Although the conductor size range in this proposal does not conform to the XLPE proposal data, the cable termination is still suitable for use with the proposed XLPE cables.
conforming with EGAT requirement (IEEE 48)
Other*
Porcelain
Other
2 x 1 bolt holes NEMA Pad
2 x 2 bolt holes NEMA Pad
2 x 3 bolt holes NEMA Pad
Other*
Medium Pollution
Heavy Pollution
| Extremely Heavy Pollution |  |  |  | Insulation Class 15 kV
| Other* |  |  |  | Insulation Class 25 kV
Insulation Class 35 kV
Other*
X